## Datasheet
Pump Data Sheet
Model | HSS-1100M | Type |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Issued Date
Item No. |  |  | Plant Name
Service |  |  | Quantity | Sets | ■ Indoor □ Out Door
Operating Condition
liquid |  | Flow | 120ℓ/min | (Ht=21m) | Min. Con. Flow | ℓ/min
Pumping Temp. | AMB. ℃ | Suct. Press. | - | Kgf/㎠ | Design Press. | 4.5Kgf/㎠
Sp. Gr. @P.T |  | Disc. Press. | - | Kgf/㎠ | Design Temp. | 80 ℃
Vap. Press. @P.T | - Kgf/㎠A | Diffr. Press. | - | Kgf/㎠
Visc. @P.T | Cp | Total Head | 30 | m
Operating Cond. | Continuous
Construction & Performance |  |  |  |  | Material
■ Horizontal □ Vertical |  | Efficiency | - |  | Casing | STS 304
Number of Stages | 1 Stage | Rated Power | 1100 | W | Impeller | STS 304
Speed | 3450 | NPSHre | 0m |  | Shaft | SM20C+STS304
Rotation | ■ CW □ CCW | (View From Driver) |  |  | O-ring | NBR
Bore | Size(Dia) | Rating | Face | Position | Diffuser | STS 304
Suction | 32mm | Kgf/㎠ |  | Front
Discharge | 25mm | Kgf/㎠ |  | Top
Impeller Type | open | ■ Single Suct. □ Double Suct. |  | Hydrostatic
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | Kgf/㎠ | min.
Shaft Seal | Sealless | Shaft Sleeve |  | Jacket | Kgf/㎠ | min.
Mounting |  |  |  | Testing
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) |  | (Witness)
Cooling | □ Stuff. Box □ B/R Housing □ No Cooling |  |  | Run Perform. | ■ Yes□ NO | ■ Yes□ NO
Radial Bearings |  | Thrust Bearing |  | Hydrostatic | □ Yes■ NO | □ Yes■ NO
Pump Driver |  |  |  |  | Spare Parts
■ Motor □ Engine □ Turbine |  | Volt./Phase/Hz | 220V/1Φ/60Hz
Maker | WILO | Motor Fr. No.
Type | Closed | Furnished by | ■ WILO □ Customer
Power | 1100W | Mounted | ■ WILO □ Customer
Pole & Speed | 2p 3450rpm | Insulation Class | ■ B □ E □ F
Accessories
□ Base Plate
□ Foundation Bolts & Nuts
□ Coupling | □ Sunflex □ Flange □ Grid |  | □ Coupling Guard
□ Press. Gauge
□ Collar or Plug for Drain & Air Vent.
□ Companion Flange
□ Special Tool |  |  |  |  | Weight
Pump/Head
Driver
[5 empty] | Total Weight | 15 Kg
※ Don't run dry

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 120(21m) | MOTOR | OUTPUT |  |  |  | W | 1100
| TOTAL HEAD | m | 30 |  | VOLTAGE |  |  |  | V | 220
| SUCTION BORE | mm | Ø32 flange |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø25 flange |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID |  |  |  | TYPE |  |  |  | closed
| MAKER | LEO |  |  | MAKER |  |  |  | WILO
[6 empty] | TYPE |  | Horizontal Single Stage
[6 empty] | MODEL |  | HSS-1100M
SERVICE
SCALE:N/S
OUTLINE DRAWING
of HSS TYPE

## Section Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  | Q'TY
1 | MOTOR ASSY | - |  |  |  | 1
2 | BRACKET-A | ALDC |  |  |  | 1
3 | BRACKET-B | GC150 |  |  |  | 1
4 | SHAFT | SM20C+STS304 |  |  |  | 1
5 | MECHANICAL SEAL | GRAPHITE-SILICON CARBIDE |  |  |  | 1
6 | SUPPROT COVER | STS304 |  |  |  | 1
7 | IMPELLER | STS304 |  |  |  | 1
8 | WASHER | STS304 |  |  |  | 1
9 | NUT | STS304 |  |  |  | 1
10 | O-RING | NBR |  |  |  | 1
11 | DIFFUSER | STS304 |  |  |  | 1
12 | PACKING | NBR |  |  |  | 1
13 | CASING | STS304 |  |  |  | 1
14 | BOLT, HEXA | STS304 |  |  |  | 8
15 | DRAIN PLUG | STS304 |  |  |  | 2
|  |  | TYPE |  | Horizontal Single Stage
|  |  | MODEL |  | HSS-1100M
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of HSS TYPE

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 63.8 | 109.3 | 137.4 | 167.5 | 194 | 225.6 | 234.4
Dis. Head | (m) | 32.3 | 28 | 24 | 21 | 17 | 13 | 7 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.15022 | 0.44089 | 0.69673 | 1.0354 | 1.389 | 1.8783 | 2.0277
Total Head | (m) | 32.3 | 28.1502 | 24.4409 | 21.6967 | 18.0354 | 14.389 | 8.8783 | 4.0277
Water Power | (㎾) | 0 | 0.29275 | 0.43544 | 0.48592 | 0.49241 | 0.45501 | 0.32648 | 0.15389
Shaft Power | (㎾) | 0.5551 | 0.7091 | 0.8435 | 0.9156 | 0.9625 | 0.994 | 0.9905 | 0.9492
Pump Eff. | (%) | 0 | 41.2841 | 51.6226 | 53.0717 | 51.1597 | 45.7755 | 32.9612 | 16.2124
Speed | (rpm) | 3523 | 3490 | 3460 | 3442 | 3431 | 3424 | 3420 | 3431
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 3.53 | 4.58 | 5.48 | 5.92 | 6.24 | 6.43 | 6.39 | 6.18
Motor Input | (㎾) | 0.793 | 1.013 | 1.205 | 1.308 | 1.375 | 1.42 | 1.415 | 1.356
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 120 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.1 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 21 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 32 | 25
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 6.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker |  | Turbin | 18 | 26
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | HSS-1100M |  | Customer |  |  |  | 0.5
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification