## Datasheet
Pump Data Sheet
Model | HSS-1500U | Type |  |  | Sheet No.
Customer |  |  | Agent No.
Location |  |  | Issued Date
Item No. |  |  | Plant Name
Service |  |  | Quantity | Sets | ■ Indoor □ Out Door
Operating Condition
liquid |  | Flow | 260ℓ/min | (Ht=18m) | Min. Con. Flow | ℓ/min
Pumping Temp. | AMB. ℃ | Suct. Press. | - | Kgf/㎠ | Design Press. | 4.5Kgf/㎠
Sp. Gr. @P.T |  | Disc. Press. | - | Kgf/㎠ | Design Temp. | 80 ℃
Vap. Press. @P.T | - Kgf/㎠A | Diffr. Press. | - | Kgf/㎠
Visc. @P.T | Cp | Total Head | 25 | m
Operating Cond. | Continuous
Construction & Performance |  |  |  |  | Material
■ Horizontal □ Vertical |  | Efficiency | - |  | Casing | STS 304
Number of Stages | 1 Stage | Rated Power | 1500 | W | Impeller | STS 304
Speed | 3450 | NPSHre | 0m |  | Shaft | SM20C+STS304
Rotation | ■ CW □ CCW | (View From Driver) |  |  | O-ring | NBR
Bore | Size(Dia) | Rating | Face | Position | Diffuser | STS 304
Suction | 40mm | Kgf/㎠ |  | Front
Discharge | 32mm | Kgf/㎠ |  | Top
Impeller Type | open | ■ Single Suct. □ Double Suct. |  | Hydrostatic
Flow Direction | ■ Radial □ Mixed □ Axial |  |  | Casing | Kgf/㎠ | min.
Shaft Seal | Sealless | Shaft Sleeve |  | Jacket | Kgf/㎠ | min.
Mounting |  |  |  | Testing
Lubrication Type | □ Grease □ Oil Bath |  |  | (Items) |  | (Witness)
Cooling | □ Stuff. Box □ B/R Housing □ No Cooling |  |  | Run Perform. | ■ Yes□ NO | ■ Yes□ NO
Radial Bearings |  | Thrust Bearing |  | Hydrostatic | □ Yes■ NO | □ Yes■ NO
Pump Driver |  |  |  |  | Spare Parts
■ Motor □ Engine □ Turbine |  | Volt./Phase/Hz | 380V/3Φ/60Hz
Maker | WILO | Motor Fr. No.
Type | Closed | Furnished by | ■ WILO □ Customer
Power | 1500W | Mounted | ■ WILO □ Customer
Pole & Speed | 2p 3450rpm | Insulation Class | □ B □ E ■ F
Accessories
□ Base Plate
□ Foundation Bolts & Nuts
□ Coupling | □ Sunflex □ Flange □ Grid |  | □ Coupling Guard
□ Press. Gauge
□ Collar or Plug for Drain & Air Vent.
□ Companion Flange
□ Special Tool |  |  |  |  | Weight
Pump/Head
Driver
[5 empty] | Total Weight | 18 Kg
※ Don't run dry

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
PUMP | CAPACITY | ℓ/min | 260(18m) | MOTOR | OUTPUT |  |  |  | W | 1500
| TOTAL HEAD | m | 25 |  | VOLTAGE |  |  |  | V | 380
| SUCTION BORE | mm | Ø40 flange |  | FREQUENCY |  |  |  | Hz | 60
| DISCHARGE BORE | mm | Ø32 flange |  | No. OF REVOLUTION |  |  |  | r.p.m | 3450
| LIQUID |  |  |  | TYPE |  |  |  | closed
| MAKER | LEO |  |  | MAKER |  |  |  | WILO
[6 empty] | TYPE |  | Horizontal Single Stage
[6 empty] | MODEL |  | HSS-1500U
SERVICE
SCALE:N/S
OUTLINE DRAWING
of HSS TYPE

## Section Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO. | PARTS NAME | MATERIALS |  |  |  | Q'TY
1 | MOTOR ASSY | - |  |  |  | 1
2 | BRACKET-A | ALDC |  |  |  | 1
3 | BRACKET-B | GC150 |  |  |  | 1
4 | SHAFT | SM20C+STS304 |  |  |  | 1
5 | MECHANICAL SEAL | GRAPHITE-SILICON CARBIDE |  |  |  | 1
6 | SUPPROT COVER | STS304 |  |  |  | 1
7 | IMPELLER | STS304 |  |  |  | 1
8 | WASHER | STS304 |  |  |  | 1
9 | NUT | STS304 |  |  |  | 1
10 | O-RING | NBR |  |  |  | 1
11 | DIFFUSER | STS304 |  |  |  | 1
12 | PACKING | NBR |  |  |  | 1
13 | CASING | STS304 |  |  |  | 1
14 | BOLT, HEXA | STS304 |  |  |  | 8
15 | DRAIN PLUG | STS304 |  |  |  | 2
|  |  | TYPE |  | Horizontal Single Stage
|  |  | MODEL |  | HSS-1500U
SERVICE
SCALE:N/S
SECTIONAL DRAWING
of HSS TYPE

## Test Report
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 151 | 281 | 325 | 363.5 | 397.5 | 432.5 | 445.3
Dis. Head | (m) | 27.5 | 24 | 18 | 15 | 12 | 9 | 6 | 4.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.29496 | 1.0215 | 1.3664 | 1.7093 | 2.044 | 2.4198 | 2.5651
Total Head | (m) | 27.5 | 24.295 | 19.0215 | 16.3664 | 13.7093 | 11.044 | 8.4198 | 6.6651
Water Power | (kW) | 0 | 0.59797 | 0.87124 | 0.86701 | 0.81228 | 0.71557 | 0.59357 | 0.48378
Shaft Power | (kW) | 0.62412 | 1.1617 | 1.475 | 1.5229 | 1.5464 | 1.554 | 1.559 | 1.5582
Pump Eff. | (%) | 0 | 51.473 | 59.0655 | 56.9307 | 52.5259 | 46.0469 | 38.0731 | 31.0475
Speed | (rpm) | 3543 | 3486 | 3448 | 3443 | 3437 | 3432 | 3431 | 3428
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.07 | 2.7 | 3.18 | 3.26 | 3.29 | 3.3 | 3.31 | 3.32
Motor Input | (kW) | 0.743 | 1.383 | 1.756 | 1.813 | 1.841 | 1.85 | 1.856 | 1.855
Motor Eff. | (%) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 260 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 18 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 40 | 32 | 0
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 84 | Maker |  | Turbin | 18 | 26
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | HSS-1500U |  | Customer |  |  |  | 0.5
Checked By |  |  |  |  | Approved By
Vacuum | mmhg
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
-5%일때의 Data |  | 26.125 | 23.0802 | 18.0704 | 15.5481 | 13.0238 | 10.4918
0 | 0.11 | 0.142 | 0.196 | 0.243 | 0.302 | 0.334 | 0.373
0 | 110 | 142 | 196 | 243 | 302 | 334 | 373
16.8 | 15 | 14 | 12 | 10 | 7 | 5 | 2.2
3519 | 3461 | 3448 | 3431 | 3415 | 3408 | 3406 | 3407
500 | 784 | 847 | 929 | 972 | 991 | 994 | 974
0.5 | 0.784 | 0.847 | 0.929 | 0.972 | 0.991 | 0.994 | 0.974
1.02 | 1.39 | 1.48 | 1.6 | 1.66 | 1.68 | 1.69 | 1.66
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification