## Datasheet(HSSI)
PUMP DATA SHEET
Model |  | HSSI-Series |  |  |  | Title |  |  |  |  | Sheet No.
Customer | [5 empty] | Agent No.
Location | [5 empty] | Date Issued
Item No. | [5 empty] | Plant Name
Service | [5 empty] | Quantity |  |  |  |  | Location |  | ■ In, □ Out
OPERATING CONDITION
Environment |  | 0~40 ℃ |  |  | Humidity |  | 95% max |  |  | Altitude |  |  | 1,000m max
Delivery Pressure |  | max.10 bar |  |  | No. of starts |  | Motor<1.5kW : 80/hr 1.5kW<Motor<2.2kW : 50/hr Motor>2.2kW : 20/hr
Running time |  | 12,000hr |  |  | Granulometry |  | Ø 0.5mm max |  |  | Kinematic viscosity |  |  | equivalent to water
Density |  | 1.03 kg/dm3 in standard |  |  | PH |  | STS304 = 6 to 9.5 (STS316L =5 to 12)
PERFORMANCE AND CONSTRUCTIONS
|  | Model | HSSI-1100MA | [5 empty] | HSSI-1500MA
Classification
Power Source (V/ph/Hz) |  |  | 220/1/60
Motor (V/Phase/Hz) |  |  | 220/3/60
Motor Input(kW) |  |  | 1.55 | [5 empty] | 2.17
Motor Output(kW) |  |  | 1.1 | [5 empty] | 1.5
Inverter Output(kW) |  |  | 1.5 | [5 empty] | 1.5
Inverter Capacity(KVA) |  |  | 3 | [5 empty] | 4.5
Inverter Input Frequency(Hz) |  |  | 50~60
Inverter Output Freq.(Hz) |  |  | max.60
Rotational Speed(rpm) |  |  | 1,440~3,600
Current (A) | Pump | 1 phase | 14 | [5 empty] | 17
| Motor | 3 phase | 4.6 | [5 empty] | 6.9
Pump Shut off Head(m) |  |  | 30 | [5 empty] | 25
Flow (m3/hr) | Rated Flow | Q | 6 | [5 empty] | 12
|  | at H(m) | 21 | [5 empty] | 18
Piping(mm) |  | Suct. | 32 | [5 empty] | 40
|  | Disch. | 25 | [5 empty] | 35
No. of Impeller Stages |  |  | 1 | [5 empty] | 1
Diameter of Impeller(mm) |  |  | 132 | [5 empty] | 122
Bearing | Pump Side |  | 6304
| Fan Side |  | 6204
Cable Gland |  |  | PG13.5
Weight (kg) |  |  | 17 | [5 empty] | 19
Mounting Position |  |  | ■ Hotizontal, □ Vertical |  |  |  |  | Suction Head(m) |  |  | Non self priming
Motor Maker |  |  | WILO (in Korea) |  |  |  |  | Insulation Class |  |  | F
Shaft Seal |  |  | □ G/Packing, ■ M/Seal |  |  |  |  | Protecting Index |  |  | IPX4
Speed |  |  | 3,400 rpm |  |  |  |  | Rotation |  |  | □ CW, ■ CCW (viewed from pump Head)
Impeller Type |  |  | Centrifugal |  |  |  |  | Flow Direction |  |  | ■ Radial, □ Mixed, □ Axial
Lubrication Type |  |  | ■ Grease, □ Oil Bath |  |  |  |  | Cooling |  |  | □ Stuff. Box, □ B/R Housing, ■ No cooling
TESTING | [7 empty] | HYDROSTATIC
( Items ) |  | ( Self test ) |  |  | ( Witness ) |  |  | Casing |  |  | 4.5 Kg/cm2 |  | 3 min
Run Performal |  | ■ Yes, □ No |  |  | □ Yes, ■ No |  |  | Pressure Tank |  |  | 20 Kg/cm2 |  | 3 min
Hydrostatic |  | ■ Yes, □ No |  |  | □ Yes, ■ No
MECHANICAL SEAL
TYPE |  |  | Ø on Shaft |  | Fitting Dimension |  | Service Limits |  |  | Materials
[10 empty] | O-Ring |  | Spring |  | O-Ring
ZY155-14 |  |  | 14 |  | 28±0.3mm |  | P ≤ 7 bar, -20℃< T <100℃ |  |  | NBR |  | STS304 |  | NBR
- |  |  | - |  | - |  | - |  |  | - |  | - |  | -
- |  |  | - |  | - |  | - |  |  | - |  | - |  | -
ACCESSORIES
■ Base plate |  |  | □ Drain Rim |  |  | □ Foundation Bolts & Nuts |  |  | ■ Plug for Priming & Screw for Drain
Coupling |  |  | □ Sun Flex □ Woods □ Grid ■ No | [5 empty] | □ Sealing Flushing Pipe □ Cooling Piping ■ No
Press. Gauge |  |  | □ Suct. Vacuum □ Suct. Compound □ Suct. Press ■ Disch. Press □ No
□ Companion Flange
□ Special Tools
SPARE PARTS
Impeller |  | Set(S) |  | Shaft Spacer |  | Set(S) |  | Shaft |  | Set(S) |  | Nipple |  | Set(S)
Bearing |  | Set(S) |  | Diffuser |  | Set(S) |  | M/Seal |  | Set(S) |  | Inverter |  | Set(S)
Casing O-Ring |  | Set(S) |  | Check Valve |  | Set(S) |  | Union |  | Set(S) |  | Sensor |  | Set(S)
Name Plate |  | Set(S) |  | Pressure Tank |  | Set(S) |  | Pressure Gauge |  | Set(S) |  | Terminal Box |  | Set(S)

## Dimension(HSSI)
Sheet No.
CUSTOMER
ITEM No.
DATE
TYPE |  | Horizontal Single Stage Pump
MODEL |  | HSSI-Series
SERVICE
SCALE : N/S
OUTLINE DRAWING
of HSSI-Series

## Sectional(HSSI)
Sheet No.
CUSTOMER
ITEM No.
DATE
Cls. | Part Name | Specification |  | Quantity | Remarks
1 | Motor Assembly | 3phase 220V 60Hz |  | 1
2 | Motor Supporter | ABS(HI-100) |  | 1
3 | Fan Cover | SCP |  | 1
4 | Base Plate | SCP |  | 1
5 | Casing | STS304 |  | 1
6 | Drain Plug | STS304 |  | 1
7 | Priming Plug | STS304 |  | 1
8 | Union Assembly | STS304 |  | 1
9 | Check Valve | STS304 |  | 1
10 | Pressure Tank | SCP/Rubber |  | 1
11 | Pressure Gauge | 15bar |  | 1
12 | Inverter Assembly | - |  | 1
13 | Inverter Cover | ABS(AF-305F) |  | 1
14 | Inverter Base | ABS(AF-305F) or ALDC |  | 1
15 | Pressure Sensor | 16bar |  | 1
16 | Power Cord | PNCT 3C |  | 1
|  |  | TYPE |  | Horizontal Single Stage Pump
|  |  | MODEL |  | HSSI-Series
SERVICE
SCALE : N/S
SECTIONAL DRAWING
of HSSI-Series

## Test Report(HSSI-1500MA)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 106 | 184 | 230 | 267.5 | 300 | 329 | 377.2
Dis. Head | (m) | 27.2 | 24 | 21 | 18 | 15 | 12 | 9 | 3.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.14535 | 0.43797 | 0.68432 | 0.92566 | 1.1643 | 1.4002 | 1.8406
Total Head | (m) | 27.2 | 24.1454 | 21.438 | 18.6843 | 15.9257 | 13.1643 | 10.4002 | 5.3406
Water Power | (㎾) | 0 | 0.41718 | 0.64297 | 0.70048 | 0.6944 | 0.64373 | 0.55773 | 0.32836
Shaft Power | (㎾) | 0.63504 | 1.0147 | 1.2768 | 1.412 | 1.5044 | 1.5607 | 1.6044 | 1.6456
Pump Eff. | (%) | 0 | 41.1132 | 50.3577 | 49.6073 | 46.1566 | 41.2458 | 34.7627 | 19.9541
Speed | (rpm) | 3534 | 3489 | 3457 | 3439 | 3426 | 3417 | 3412 | 3404
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.54 | 11.48 | 14.11 | 15.46 | 16.35 | 16.89 | 17.31 | 17.74
Motor Input | (㎾) | 0.756 | 1.208 | 1.52 | 1.681 | 1.791 | 1.858 | 1.91 | 1.959
Motor Eff. | (%) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 200 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 18 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 | 40 | 32 | 0
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 17 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 84 | Maker | WILO | Turbin | 11 | 13
Item No. |  |  | Serial No. |  | Inspector | KJO | Run (Hr) | B/R (℃) | Test Date
Model | HSSI-1500MA |  | Customer |  |  |  | 2 | 34
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Data (hidden)
No. | Model | Capa.(ℓ/min.) | Head(m) | Power Supply | Output | Disharge | Pole | RPM | Impeller Type | Suction | Casing Mat'l | Impeller Mat'l | Shaft Mat'l | Flange Mat'l | Capa1 | Capa2 | Capa3 | Capa4 | Capa5 | Head1 | Head2 | Head3 | Head4 | Head5 | SP1 | SP2 | SP3 | SP4 | SP5 | Eff1 | Eff2 | Eff3 | Eff4 | Eff5 | 380V Amp.
1 | PU-756M | 200(at Ht 6m) | 35 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Semi-Open □ Open | 50(2") | GC150 | C3771BD | STS410 | GC200 | 0 | 107.7 | 172 | 227.5 | 233 | 21.7 | 18 | 14 | 8 | 6.5 | 0.35 | 0.51 | 0.59 | 0.63 | 0.62 | 0 | 61.83 | 66.51 | 47.21 | 39.59 | 8
2 | PW-K130MA | 200(at Ht 6m) | 35 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Semi-Open □ Open | 50(2") | GC150 | C3771BD | STS410 | GC200 | 0 | 107.7 | 172 | 227.5 | 233 | 21.7 | 18 | 14 | 8 | 6.5 | 0.35 | 0.51 | 0.59 | 0.63 | 0.62 | 0 | 61.83 | 66.51 | 47.21 | 39.59 | 8
3 | PW-409MA | 32(at Ht 12m) | 30 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 8.1 | 16.7 | 28.5 | 38 | 55 | 46 | 36 | 21 | 9 | 0.6 | 0.55 | 0.47 | 0.37 | 0.3 | 0 | 11.12 | 20.82 | 26.38 | 18.59 | 8
4 | PW-405M | 40(at Ht 12m) | 36 | 1Phase 220V 60Hz | 400 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 30(1 1/4") | GC150 | C3771BD | STS410 | GC200 | 0 | 10 | 31 | 41 | 46 | 53 | 46 | 26 | 16 | 9.5 | 0.73 | 0.65 | 0.46 | 0.39 | 0.34 | 0 | 11.48 | 28.68 | 27.55 | 20.94 | 8
5 | PW-804MA | 45(at Ht 12m) | 33 | 1Phase 220V 60Hz | 750 | Clean Water | 2 | 3400 | □ Closed ■ Westo □ Open | 40(1 1/2") | GC150 | C3771BD | STS410 | GC200 | 0 | 15 | 32 | 46 | 50 | 74 | 56 | 34 | 16 | 12 | 0.99 | 0.85 | 0.67 | 0.54 | 0.52 | 0 | 16.14 | 26.51 | 22.15 | 18.88 | 8