## Datasheet(PLS-1012GP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-1012GP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 90 | m | Shaft | STS410
10 | Rated Capacity | 35 | ℓ/min | Shell | STS304
11 | Shut off Head | 130 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 15 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 45 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 9.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 14 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 530 | mm | Pump | 3.8 | kg
37 | Motor | 299 | mm | Motor | 10.9 | kg
38 | Total | 829 | mm | Total | 14.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-2012GP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-2012GP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 150 | m | Shaft | STS410
10 | Rated Capacity | 35 | ℓ/min | Shell | STS304
11 | Shut off Head | 220 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 15 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 45 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 13.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 24 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 774 | mm | Pump | 4.3 | kg
37 | Motor | 385 | mm | Motor | 14.5 | kg
38 | Total | 1159 | mm | Total | 18.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-2032GP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-2032GP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 150 | m | Shaft | STS410
10 | Rated Capacity | 35 | ℓ/min | Shell | STS304
11 | Shut off Head | 220 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 15 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 45 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 8.1 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 24 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 774 | mm | Pump | 4.3 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 1120 | mm | Total | 17.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-2033GP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-2033GP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 150 | m | Shaft | STS410
10 | Rated Capacity | 35 | ℓ/min | Shell | STS304
11 | Shut off Head | 220 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 15 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 45 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 4.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 24 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 774 | mm | Pump | 4.3 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 1120 | mm | Total | 17.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-3012G)
Submersible Motor Pump Data Sheet
1 | Model | PLS-3012G | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 190 | m | Shaft | STS410
10 | Rated Capacity | 35 | ℓ/min | Shell | STS304
11 | Shut off Head | 290 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 45 | % | Sleeve | STS304
14 | Min. Flow | 15 | ℓ/min | Head | HBsC1
15 | Max. Flow | 45 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 1phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 17 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 32 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 970 | mm | Pump | 8.8 | kg
37 | Motor | 602 | mm | Motor | 25 | kg
38 | Total | 1572 | mm | Total | 33.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-3032G)
Submersible Motor Pump Data Sheet
1 | Model | PLS-3032G | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 190 | m | Shaft | STS410
10 | Rated Capacity | 35 | ℓ/min | Shell | STS304
11 | Shut off Head | 290 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 45 | % | Sleeve | STS304
14 | Min. Flow | 15 | ℓ/min | Head | HBsC1
15 | Max. Flow | 45 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 32 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 970 | mm | Pump | 8.8 | kg
37 | Motor | 524 | mm | Motor | 20 | kg
38 | Total | 1494 | mm | Total | 28.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-3033G)
Submersible Motor Pump Data Sheet
1 | Model | PLS-3033G | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 190 | m | Shaft | STS410
10 | Rated Capacity | 35 | ℓ/min | Shell | STS304
11 | Shut off Head | 290 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 45 | % | Sleeve | STS304
14 | Min. Flow | 15 | ℓ/min | Head | HBsC1
15 | Max. Flow | 45 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 6.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 32 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 970 | mm | Pump | 8.8 | kg
37 | Motor | 524 | mm | Motor | 20 | kg
38 | Total | 1494 | mm | Total | 28.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE |  | VOLTS | HZ
PLS-1012GP | 14 |  |  | 1 |  | 1 |  | 220 | 60
PLS-2012GP | 24 |  |  | 2 |  | 1 |  | 220 | 60
PLS-2032GP | 24 | 28 |  | 2 |  | 3 |  | 220 | 60
PLS-2033GP | 24 | 37 |  | 2 |  | 3 |  | 380 | 60
PLS-3012G | 32 |  |  | 3 |  | 3 |  | 220 | 60
PLS-3032G | 32 |  |  | 3 |  | 3 |  | 220 | 60
PLS-3033G | 32 |  |  | 3 |  | 3 |  | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PLS-1012GP | 520 |  |  | 300 |  |  | 820
PLS-2012GP | 774 |  |  | 385 |  |  | 1159
PLS-2032GP | 774 | 28 |  | 346 |  |  | 1120
PLS-2033GP | 774 | 37 |  | 346 |  |  | 1120
PLS-3012G | 970 |  |  | 602 |  |  | 1572
PLS-3032G | 970 |  |  | 524 |  |  | 1494
PLS-3033G | 970 |  |  | 524 |  |  | 1494
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PLS-1012GP | 4.5 |  |  | 10.9 |  |  | 15.4
PLS-2012GP | 6 |  |  | 14.5 |  |  | 20.5
PLS-2032GP | 6 | 28 |  | 13.1 |  |  | 19.1
PLS-2033GP | 6 | 37 |  | 13.1 |  |  | 19.1
PLS-3012G | 8.8 |  |  | 25 |  |  | 33.8
PLS-3032G | 8.8 |  |  | 20 |  |  | 28.8
PLS-3033G | 8.8 |  |  | 20 |  |  | 28.8
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
|  | TYPE |  |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PLS-GP,HP TYPE
104mm
P.L
M.L
T.L
Cable Guard
Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD,PUMP |  |  | POM + BRASS |  | 1
2 | STOP RING |  |  | STS304 |  | 1
3 | CHECK VALVE |  |  | NORYL + NBR |  | 1
4 | FIXING NUT |  |  | STS304 + NYLON |  | 1
5 | PLAIN WASHER |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | SLIDING BEARING |  |  | NBR |  | 1
8 | DIFFUSER |  |  | NORYL |  | Stages
9 | SLIDING BEARING |  |  | NBR |  | Stages
10 | UPTHRUST WASHER |  |  | STS304 |  | Stages
11 | MIDDLE CASING |  |  | NORYL |  | Stages
12 | IMPELLER |  |  | NORYL+STS304 |  | Stages
13 | IMPELLER GASKET |  |  | NBR |  | Stages
14 | MIDDLE SPACER |  |  | NORYL |  | 1~2
15 | SLEEVE |  |  | STS304 |  | 1~2
16 | SLIDING BEARING |  |  | NBR |  | 1~2
17 | SHELL |  |  | STS304 |  | 1
18 | LOWER SPACER |  |  | NORYL |  | 1
19 | SHAFT |  |  | STS410 |  | 1
20 | COUPLING |  |  | STS304 |  | 1
21 | SCREW |  |  | STS304 |  | 1
22 | STOPPER |  |  | STS304 |  | 1
23 | BASE |  |  | NORYL |  | 1
24 | SCREW |  |  | STS304 |  | 1
25 | CABLE GUARD |  |  | HD PE |  | 1
26 | STRAINER |  |  | STS304 |  | 1
27 | SCREW |  |  | STS304 |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PLS-GP,HP TYPE
22
27
26
23
24
25
13
20
21
18
16
15
14
12
3
19
17
7
11
10
8
9
5
6
4
1
2

## Test Report(PLS-1012GP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 15 | 25 | 35 | 45 | 55 | 66
Dis. Head | (m) | 132 | 122 | 110 | 94 | 71 | 45 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0049299 | 0.013694 | 0.026841 | 0.044369 | 0.06628 | 0.095444
Total Head | (m) | 133.55 | 123.5549 | 111.5637 | 95.5768 | 72.5944 | 46.6163 | 1.6454
Water Power | (㎾) | 0 | 0.30209 | 0.45462 | 0.54527 | 0.53248 | 0.41791 | 0.017702
Shaft Power | (㎾) | 0.61074 | 0.86444 | 0.93562 | 0.96432 | 0.96317 | 0.93045 | 0.90003
Pump Eff. | (%) | 0 | 34.9464 | 48.5905 | 56.5441 | 55.284 | 44.9152 | 1.9668
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.37 | 8.87 | 9.34 | 9.54 | 9.52 | 9.29 | 9.1
Motor Input | (㎾) | 1.064 | 1.506 | 1.63 | 1.68 | 1.678 | 1.621 | 1.568
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 80 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1.55
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | FRANKLIN | Turbin | 26 | 26
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-1012GP |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-2012GP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20 | 35 | 40 | 50 | 60 | 73
Dis. Head | (m) | 222 | 195 | 165 | 152 | 115 | 72 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0087643 | 0.026841 | 0.035057 | 0.054777 | 0.078879 | 0.11676
Total Head | (m) | 223.65 | 196.6588 | 166.6768 | 153.6851 | 116.7048 | 73.7289 | 1.7668
Water Power | (㎾) | 0 | 0.64111 | 0.95089 | 1.002 | 0.95114 | 0.72107 | 0.021023
Shaft Power | (㎾) | 1.0912 | 1.7152 | 1.8218 | 1.8294 | 1.8225 | 1.7393 | 1.6622
Pump Eff. | (%) | 0 | 37.3784 | 52.1945 | 54.7737 | 52.1886 | 41.4583 | 1.2647
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.72 | 11.85 | 12.56 | 12.57 | 12.59 | 12.03 | 11.51
Motor Input | (㎾) | 1.586 | 2.493 | 2.648 | 2.659 | 2.649 | 2.528 | 2.416
Motor Eff. | (%) | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 130 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1.65
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 13.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68.8 | Maker | FRANKLIN | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-2012GP |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-2032GP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20 | 35 | 40 | 50 | 60 | 74
Dis. Head | (m) | 222 | 194 | 163 | 146 | 110 | 65 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0087643 | 0.026841 | 0.035057 | 0.054777 | 0.078879 | 0.11998
Total Head | (m) | 223.65 | 195.6588 | 164.6768 | 147.6851 | 111.7048 | 66.7289 | 1.77
Water Power | (㎾) | 0 | 0.63785 | 0.93948 | 0.96291 | 0.91039 | 0.65261 | 0.02135
Shaft Power | (㎾) | 1.0894 | 1.6162 | 1.7088 | 1.7159 | 1.7017 | 1.6305 | 1.5949
Pump Eff. | (%) | 0 | 39.4649 | 54.979 | 56.1161 | 53.4997 | 40.0255 | 1.3386
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 5.4 | 7 | 7.35 | 7.38 | 7.32 | 7.05 | 6.92
Motor Input | (㎾) | 1.53 | 2.27 | 2.4 | 2.41 | 2.39 | 2.29 | 2.24
Motor Eff. | (%) | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 130 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1.65
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 8.1 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 71.2 | Maker | FRANKLIN | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-2032GP |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-2033GP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20 | 35 | 40 | 50 | 60 | 75
Dis. Head | (m) | 220 | 195 | 164 | 150 | 110 | 66 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0087643 | 0.026841 | 0.035057 | 0.054777 | 0.078879 | 0.12325
Total Head | (m) | 221.65 | 196.6588 | 165.6768 | 151.6851 | 111.7048 | 67.7289 | 1.7732
Water Power | (㎾) | 0 | 0.64111 | 0.94519 | 0.98899 | 0.91039 | 0.66239 | 0.021678
Shaft Power | (㎾) | 1.2246 | 1.6946 | 1.7658 | 1.7658 | 1.7373 | 1.659 | 1.6162
Pump Eff. | (%) | 0 | 37.8333 | 53.5286 | 56.0091 | 52.4034 | 39.9279 | 1.3413
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.57 | 4.38 | 4.51 | 4.54 | 4.49 | 4.34 | 4.28
Motor Input | (㎾) | 1.72 | 2.38 | 2.48 | 2.48 | 2.44 | 2.33 | 2.27
Motor Eff. | (%) | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 130 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1.65
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 71.2 | Maker | FRANKLIN | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-2033GP |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-3012G)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 15 | 35 | 40 | 50 | 60 | 69
Dis. Head | (m) | 298 | 276 | 212 | 188 | 135 | 65 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0049299 | 0.026841 | 0.035057 | 0.054777 | 0.078879 | 0.10432
Total Head | (m) | 299.6 | 277.6049 | 213.6268 | 189.6351 | 136.6548 | 66.6789 | 1.7043
Water Power | (㎾) | 0 | 0.67874 | 1.2187 | 1.2364 | 1.1137 | 0.65212 | 0.019168
Shaft Power | (㎾) | 1.8144 | 2.3737 | 2.5606 | 2.548 | 2.4892 | 2.3583 | 2.3254
Pump Eff. | (%) | 0 | 28.5943 | 47.5959 | 48.5251 | 44.7427 | 27.6521 | 0.82431
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 12.04 | 15.77 | 16.85 | 16.8 | 16.41 | 15.51 | 15.34
Motor Input | (㎾) | 2.592 | 3.391 | 3.658 | 3.64 | 3.556 | 3.369 | 3.322
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 190 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1.6
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 17.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | FRANKLIN | Turbin | 26 | 26
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-3012GP |  | Customer |  |  |  | 2 |  | 00/5/15
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-3032G)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 15 | 35 | 40 | 50 | 60 | 69
Dis. Head | (m) | 296 | 275 | 210 | 185 | 132 | 61 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0049299 | 0.026841 | 0.035057 | 0.054777 | 0.078879 | 0.10432
Total Head | (m) | 297.6 | 276.6049 | 211.6268 | 186.6351 | 133.6548 | 62.6789 | 1.7043
Water Power | (㎾) | 0 | 0.6763 | 1.2073 | 1.2169 | 1.0893 | 0.613 | 0.019168
Shaft Power | (㎾) | 1.8973 | 2.4822 | 2.6777 | 2.6645 | 2.603 | 2.4661 | 2.4317
Pump Eff. | (%) | 0 | 27.2458 | 45.0891 | 45.6697 | 41.8475 | 24.857 | 0.78827
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 8.7 | 9.89 | 10.19 | 10.21 | 9.96 | 9.6 | 9.45
Motor Input | (㎾) | 2.592 | 3.391 | 3.658 | 3.64 | 3.556 | 3.369 | 3.322
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 190 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1.6
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 10.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin | 26 | 26
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-3032GP |  | Customer |  |  |  | 2 |  | 00/5/15
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-3033G)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 15 | 35 | 40 | 50 | 60 | 68
Dis. Head | (m) | 300 | 270 | 215 | 195 | 145 | 68 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0049299 | 0.026841 | 0.035057 | 0.054777 | 0.078879 | 0.10132
Total Head | (m) | 301.6 | 271.6049 | 216.6268 | 196.6351 | 146.6548 | 69.6789 | 1.7013
Water Power | (㎾) | 0 | 0.66407 | 1.2359 | 1.2821 | 1.1952 | 0.68146 | 0.018857
Shaft Power | (㎾) | 1.6836 | 2.3351 | 2.4376 | 2.4522 | 2.4083 | 2.2546 | 2.2472
Pump Eff. | (%) | 0 | 28.439 | 50.7005 | 52.2821 | 49.6303 | 30.2258 | 0.83914
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 5.03 | 6.1 | 6.29 | 6.3 | 6.23 | 5.98 | 5.95
Motor Input | (㎾) | 2.3 | 3.19 | 3.33 | 3.35 | 3.29 | 3.08 | 3.07
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 190 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1.6
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin | 26 | 26
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-3033GP |  | Customer |  |  |  | 2 |  | 00/5/15
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification