## Datasheet(PLS-1012HP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-1012HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 45 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 80 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 9.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 390 | mm | Pump | 2.5 | kg
37 | Motor | 299 | mm | Motor | 10.9 | kg
38 | Total | 689 | mm | Total | 13.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-2012HP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-2012HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 80 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 125 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 13.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 555 | mm | Pump | 4.3 | kg
37 | Motor | 385 | mm | Motor | 14.5 | kg
38 | Total | 940 | mm | Total | 18.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-2032HP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-2032HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 80 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 125 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 8.1 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 555 | mm | Pump | 4.3 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 901 | mm | Total | 17.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-2033HP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-2033HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 80 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 125 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 4.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 555 | mm | Pump | 4.3 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 901 | mm | Total | 17.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-3012HP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-3012HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 105 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 165 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 17 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 685 | mm | Pump | 5.5 | kg
37 | Motor | 550 | mm | Motor | 20 | kg
38 | Total | 1235 | mm | Total | 25.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-3032HP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-3032HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 105 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 165 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 685 | mm | Pump | 5.5 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 1185 | mm | Total | 22.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-3033HP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-3033HP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 105 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 165 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 100 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 6.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 685 | mm | Pump | 5.5 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 1185 | mm | Total | 22.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-5032H)
Submersible Motor Pump Data Sheet
1 | Model | PLS-5032H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 200 | m | Shaft | STS410
10 | Rated Capacity | 70 | ℓ/min | Shell | STS304
11 | Shut off Head | 260 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | HBsC1
15 | Max. Flow | 100 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 17.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 28 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 980 | mm | Pump | 8.9 | kg
37 | Motor | 602 | mm | Motor | 25 | kg
38 | Total | 1582 | mm | Total | 33.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-5033H)
Submersible Motor Pump Data Sheet
1 | Model | PLS-5033H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 200 | m | Shaft | STS410
10 | Rated Capacity | 70 | ℓ/min | Shell | STS304
11 | Shut off Head | 260 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | HBsC1
15 | Max. Flow | 100 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS410
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 28 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 980 | mm | Pump | 8.9 | kg
37 | Motor | 602 | mm | Motor | 25 | kg
38 | Total | 1582 | mm | Total | 33.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS4-7532H)
Submersible Motor Pump Data Sheet
1 | Model | PLS4-7532H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 230 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 360 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | HBsC1
15 | Max. Flow | 100 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 26.4 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 37 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1250 | mm | Pump | 10.5 | kg
37 | Motor | 753 | mm | Motor | 31.8 | kg
38 | Total | 2003 | mm | Total | 42.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS4-7533H)
Submersible Motor Pump Data Sheet
1 | Model | PLS4-7533H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 230 | m | Shaft | STS410
10 | Rated Capacity | 80 | ℓ/min | Shell | STS304
11 | Shut off Head | 360 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 40 | ℓ/min | Head | HBsC1
15 | Max. Flow | 100 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 16 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 37 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1250 | mm | Pump | 10.5 | kg
37 | Motor | 753 | mm | Motor | 31.8 | kg
38 | Total | 2003 | mm | Total | 42.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE |  | VOLTS | HZ
PLS-1012GP | 14 |  |  | 1 |  | 1 |  | 220 | 60
PLS-1012HP | 8 |  |  | 1 |  | 1 |  | 220 | 60
PLS-2012GP | 24 |  |  | 2 |  | 1 |  | 220 | 60
PLS-2012HP | 13 | 28 |  | 2 |  | 1 |  | 220 | 60
PLS-2032GP | 24 | 28 |  | 2 |  | 3 |  | 220 | 60
PLS-2032HP | 13 | 37 |  | 2 |  | 3 |  | 220 | 60
PLS-2033GP | 24 | 37 |  | 2 |  | 3 |  | 380 | 60
PLS-2033HP | 13 |  |  | 2 |  | 3 |  | 380 | 60
PLS-3012HP | 17 | 28 |  | 3 |  | 1 |  | 220 | 60
PLS-3032HP | 17 | 28 |  | 3 |  | 3 |  | 220 | 60
PLS-3033HP | 17 | 37 |  | 3 |  | 3 |  | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PLS-1012GP | 520 |  |  | 300 |  |  | 820
PLS-1012HP | 416 |  |  | 300 |  |  | 716
PLS-2012GP | 774 |  |  | 385 |  |  | 1159
PLS-2012HP | 555 | 28 |  | 385 |  |  | 940
PLS-2032GP | 774 | 28 |  | 346 |  |  | 1120
PLS-2032HP | 555 | 37 |  | 346 |  |  | 901
PLS-2033GP | 774 | 37 |  | 346 |  |  | 1120
PLS-2033HP | 555 |  |  | 346 |  |  | 901
PLS-3012HP | 685 | 28 |  | 560 |  |  | 1245
PLS-3032HP | 685 | 28 |  | 500 |  |  | 1185
PLS-3033HP | 685 | 37 |  | 500 |  |  | 1185
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PLS-1012GP | 4.5 |  |  | 10.9 |  |  | 15.4
PLS-1012HP | 3 |  |  | 10.9 |  |  | 13.9
PLS-2012GP | 6 |  |  | 14.5 |  |  | 20.5
PLS-2012HP | 4.3 | 28 |  | 14.5 |  |  | 18.8
PLS-2032GP | 6 | 28 |  | 13.1 |  |  | 19.1
PLS-2032HP | 4.3 | 37 |  | 13.1 |  |  | 17.4
PLS-2033GP | 6 | 37 |  | 13.1 |  |  | 19.1
PLS-2033HP | 4.3 |  |  | 13.1 |  |  | 17.4
PLS-3012HP | 5.5 | 28 |  | 20 |  |  | 25.5
PLS-3032HP | 5.5 | 28 |  | 17 |  |  | 22.5
PLS-3033HP | 5.5 | 37 |  | 17 |  |  | 22.5
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
|  | TYPE |  |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PLS-GP,HP TYPE
104mm
P.L
M.L
T.L
Cable Guard
Included

## Outline Drawing (2)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE | VOLTS | HZ
PLS-3012G | 32 |  |  | 3 |  | 1 | 220 | 60
PLS-3032G | 32 |  |  | 3 |  | 3 | 220 | 60
PLS-3033G | 32 |  |  | 3 |  | 3 | 380 | 60
PLS-5032H | 28 | 28 |  | 5 |  | 3 | 220 | 60
PLS-5033H | 28 | 28 |  | 5 |  | 3 | 380 | 60
PLS4-7532H | 37 | 37 |  | 7.5 |  | 3 | 220 | 60
PLS4-7533H | 37 | 37 |  | 7.5 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PLS-3012G | 970 |  |  | 602 |  |  | 1572
PLS-3032G | 970 |  |  | 524 |  |  | 1494
PLS-3033G | 970 |  |  | 524 |  |  | 1494
PLS-5032H | 980 |  |  | 602 |  |  | 1582
PLS-5033H | 980 |  |  | 602 |  |  | 1582
PLS4-7532H | 1250 |  |  | 753 |  |  | 2003
PLS4-7533H | 1250 | 37 |  | 753 |  |  | 2003
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PLS-3012G | 8.8 |  |  | 25 |  |  | 33.8
PLS-3032G | 8.8 |  |  | 20 |  |  | 28.8
PLS-3033G | 8.8 |  |  | 20 |  |  | 28.8
PLS-5032H | 8.9 |  |  | 25 |  |  | 33.9
PLS-5033H | 8.9 |  |  | 25 |  |  | 33.9
PLS4-7532H | 10.5 |  |  | 31.8 |  |  | 42.3
PLS4-7533H | 10.5 | 37 |  | 31.8 |  |  | 42.3
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE DIA. : 32mm
|  | TYPE |  |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PLS-G,H TYPE
104mm
P.L
M.L
T.L
Cable Guard
Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD,PUMP |  |  | POM + BRASS |  | 1
2 | STOP RING |  |  | STS304 |  | 1
3 | CHECK VALVE |  |  | NORYL + NBR |  | 1
4 | FIXING NUT |  |  | STS304 + NYLON |  | 1
5 | PLAIN WASHER |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | SLIDING BEARING |  |  | NBR |  | 1
8 | DIFFUSER |  |  | NORYL |  | Stages
9 | SLIDING BEARING |  |  | NBR |  | Stages
10 | UPTHRUST WASHER |  |  | STS304 |  | Stages
11 | MIDDLE CASING |  |  | NORYL |  | Stages
12 | IMPELLER |  |  | NORYL+STS304 |  | Stages
13 | IMPELLER GASKET |  |  | NBR |  | Stages
14 | MIDDLE SPACER |  |  | NORYL |  | 1~2
15 | SLEEVE |  |  | STS304 |  | 1~2
16 | SLIDING BEARING |  |  | NBR |  | 1~2
17 | SHELL |  |  | STS304 |  | 1
18 | LOWER SPACER |  |  | NORYL |  | 1
19 | SHAFT |  |  | STS410 |  | 1
20 | COUPLING |  |  | STS304 |  | 1
21 | SCREW |  |  | STS304 |  | 1
22 | STOPPER |  |  | STS304 |  | 1
23 | BASE |  |  | NORYL |  | 1
24 | SCREW |  |  | STS304 |  | 1
25 | CABLE GUARD |  |  | HD PE |  | 1
26 | STRAINER |  |  | STS304 |  | 1
27 | SCREW |  |  | STS304 |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PLS-GP,HP TYPE
22
27
26
23
24
25
13
20
21
18
16
15
14
12
3
19
17
7
11
10
8
9
5
6
4
1
2

## Sectional Drawing (2)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD,PUMP |  |  | BRASS |  | 1
2 | STOP RING |  |  | STS304 |  | 1
3 | CHECK VALVE |  |  | NORYL + NBR |  | 1
4 | FIXING NUT |  |  | STS304 + NYLON |  | 1
5 | PLAIN WASHER |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | SLIDING BEARING |  |  | NBR |  | 1
8 | SLEEVE |  |  | STS304 |  | 1
9 | DIFFUSER |  |  | NORYL |  | Stages
10 | SLIDING BEARING |  |  | NBR |  | Stages
11 | UPTHRUST WASHER |  |  | STS304 |  | Stages
12 | MIDDLE CASING |  |  | NORYL |  | Stages
13 | IMPELLER |  |  | NORYL+STS304 |  | Stages
14 | IMPELLER GASKET |  |  | NBR |  | Stages
15 | MIDDLE SPACER |  |  | NORYL |  | 1~2
16 | SLEEVE |  |  | STS304 |  | 1~2
17 | SLIDING BEARING |  |  | NBR |  | 1~2
18 | SHELL |  |  | STS304 |  | 1
19 | LOWER SPACER |  |  | NORYL |  | 1
20 | SHAFT |  |  | STS410 |  | 1
21 | COUPLING |  |  | STS304 |  | 1
22 | SCREW |  |  | STS304 |  | 1
23 | STOP RING |  |  | STS304 |  | 1
24 | BASE |  |  | BRASS |  | 1
25 | STRAINER |  |  | STS304 |  | 1
26 | SCREW |  |  | STS304 |  | 6
27 | CABLE GUARD |  |  | STS304 |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PLS-G,H TYPE
13
25
24
26
21
23
22
12
19
14
20
18
27
7
11
16
17
15
9
10
8
6
5
4
3
2
1

## Test Reprt(PLS-1012HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40 | 60 | 80 | 100 | 123
Dis. Head | (m) | 82 | 69.5 | 59.8 | 45.3 | 28 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.035057 | 0.078879 | 0.14023 | 0.21911 | 0.33149
Total Head | (m) | 82.7 | 70.2351 | 60.5789 | 46.1402 | 28.9191 | 1.0315
Water Power | (㎾) | 0 | 0.45793 | 0.59246 | 0.60167 | 0.47138 | 0.02068
Shaft Power | (㎾) | 0.70774 | 0.83173 | 0.92414 | 0.99876 | 1.0447 | 1.0217
Pump Eff. | (%) | 0 | 55.0581 | 64.1095 | 60.2416 | 45.1221 | 2.0241
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.63 | 8.43 | 9.01 | 9.5 | 10.03 | 9.7
Motor Input | (㎾) | 1.233 | 1.449 | 1.61 | 1.74 | 1.82 | 1.78
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 60 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 48 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | FRANKLIN | Turbin | 13 | 20
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-1012HP |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-2012HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 80 | 100 | 120 | 137
Dis. Head | (m) | 127 | 115 | 104 | 85 | 62 | 35 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.078879 | 0.14023 | 0.21911 | 0.31552 | 0.41124
Total Head | (m) | 127.75 | 115.7697 | 104.8289 | 85.8902 | 62.9691 | 36.0655 | 4.1612
Water Power | (㎾) | 0 | 0.56611 | 1.0252 | 1.12 | 1.0264 | 0.70544 | 0.092925
Shaft Power | (㎾) | 0.93843 | 1.4304 | 1.6705 | 1.7537 | 1.7269 | 1.6643 | 1.5989
Pump Eff. | (%) | 0 | 39.5786 | 61.3738 | 63.865 | 59.4365 | 42.3874 | 5.8117
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.83 | 10.15 | 11.83 | 12.45 | 12.23 | 11.75 | 11.27
Motor Input | (㎾) | 1.364 | 2.079 | 2.428 | 2.549 | 2.51 | 2.419 | 2.324
Motor Eff. | (%) | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 75 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.75
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 13.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68.8 | Maker | FRANKLIN | Turbin | 17 | 17
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-2012HP |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-2032HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 80 | 100 | 130 | 149
Dis. Head | (m) | 125 | 114 | 105 | 90 | 70 | 32 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.078879 | 0.14023 | 0.21911 | 0.37029 | 0.48644
Total Head | (m) | 125.65 | 114.6697 | 105.7289 | 90.7902 | 70.8691 | 33.0203 | 1.1364
Water Power | (㎾) | 0 | 0.56073 | 1.034 | 1.1839 | 1.1552 | 0.6997 | 0.027601
Shaft Power | (㎾) | 0.98256 | 1.3549 | 1.6006 | 1.7067 | 1.7401 | 1.6882 | 1.6234
Pump Eff. | (%) | 0 | 41.3846 | 64.6035 | 69.3695 | 66.384 | 41.4477 | 1.7002
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 5.15 | 6.21 | 6.99 | 7.34 | 7.47 | 7.32 | 7.1
Motor Input | (㎾) | 1.38 | 1.903 | 2.248 | 2.397 | 2.444 | 2.371 | 2.28
Motor Eff. | (%) | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 60 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 75 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.65
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 8.1 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 71.2 | Maker | FRANKLIN | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-2032HP |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-2033HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 80 | 100 | 130 | 150
Dis. Head | (m) | 125 | 115 | 106 | 92 | 73 | 35 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.078879 | 0.14023 | 0.21911 | 0.37029 | 0.49299
Total Head | (m) | 125.65 | 115.6697 | 106.7289 | 92.7902 | 73.8691 | 36.0203 | 1.143
Water Power | (㎾) | 0 | 0.56562 | 1.0438 | 1.21 | 1.2041 | 0.76327 | 0.027946
Shaft Power | (㎾) | 1.0039 | 1.3813 | 1.6305 | 1.723 | 1.7586 | 1.7088 | 1.659
Pump Eff. | (%) | 0 | 40.9493 | 64.0185 | 70.2238 | 68.4658 | 44.667 | 1.6846
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.19 | 3.78 | 4.2 | 4.37 | 4.46 | 4.39 | 4.32
Motor Input | (㎾) | 1.41 | 1.94 | 2.29 | 2.42 | 2.47 | 2.4 | 2.33
Motor Eff. | (%) | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 60 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 75 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.65
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 71.2 | Maker | FRANKLIN | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-2033HP |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-3012HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 31 | 60 | 80 | 114 | 140
Dis. Head | (m) | 165 | 150 | 134.5 | 112.5 | 60 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.021056 | 0.078879 | 0.14023 | 0.28475 | 0.42945
Total Head | (m) | 165.7 | 150.7211 | 135.2789 | 113.3402 | 60.9848 | 1.1295
Water Power | (㎾) | 0 | 0.76159 | 1.323 | 1.478 | 1.1332 | 0.025774
Shaft Power | (㎾) | 1.3797 | 1.9439 | 2.2722 | 2.3681 | 2.3156 | 2.1693
Pump Eff. | (%) | 0 | 39.1786 | 58.2267 | 62.4111 | 48.9384 | 1.1881
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 9.5 | 13.29 | 15.6 | 16.25 | 15.92 | 14.89
Motor Input | (㎾) | 1.971 | 2.777 | 3.246 | 3.383 | 3.308 | 3.099
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 105 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 17 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | FRANKLIN | Turbin | 11 | 14
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-3012HP |  | Customer |  |  |  | 3
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-3032HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 80 | 100 | 120 | 135
Dis. Head | (m) | 169 | 153 | 133 | 110 | 80 | 43 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.078879 | 0.14023 | 0.21911 | 0.31552 | 0.39933
Total Head | (m) | 169.7 | 153.7197 | 133.7789 | 110.8402 | 80.9191 | 44.0155 | 5.0993
Water Power | (㎾) | 0 | 0.75169 | 1.3084 | 1.4454 | 1.319 | 0.86094 | 0.11221
Shaft Power | (㎾) | 1.3059 | 1.8878 | 2.2304 | 2.2919 | 2.2956 | 2.2033 | 2.1133
Pump Eff. | (%) | 0 | 39.8177 | 58.6601 | 63.0639 | 57.4581 | 39.0748 | 5.3098
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.94 | 8.51 | 9.6 | 9.83 | 9.9 | 9.49 | 9.23
Motor Input | (㎾) | 1.784 | 2.579 | 3.047 | 3.131 | 3.136 | 3.01 | 2.887
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 105 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 10.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin | 25 | 25
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-3032HP |  | Customer |  |  |  | 3
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-3033HP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 80 | 100 | 120 | 138
Dis. Head | (m) | 167 | 153 | 136.5 | 114 | 82 | 42 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.078879 | 0.14023 | 0.21911 | 0.31552 | 0.41727
Total Head | (m) | 167.7 | 153.7197 | 137.2789 | 114.8402 | 82.9191 | 43.0155 | 1.1173
Water Power | (㎾) | 0 | 0.75169 | 1.3426 | 1.4975 | 1.3516 | 0.84138 | 0.025132
Shaft Power | (㎾) | 1.3249 | 1.8959 | 2.2326 | 2.3204 | 2.3278 | 2.2472 | 2.1814
Pump Eff. | (%) | 0 | 39.6486 | 60.1356 | 64.5359 | 58.0636 | 37.4407 | 1.1521
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.43 | 5.25 | 5.84 | 5.98 | 5.99 | 5.87 | 5.76
Motor Input | (㎾) | 1.81 | 2.59 | 3.05 | 3.17 | 3.18 | 3.07 | 2.98
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 105 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin | 21 | 16
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-3033HP |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-5032H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 90 | 120 | 140 | 150
Dis. Head | (m) | 267 | 252 | 230 | 195 | 118.3 | 50 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.078879 | 0.17748 | 0.31552 | 0.42945 | 0.49299
Total Head | (m) | 267.65 | 252.6697 | 230.7289 | 195.8275 | 119.2655 | 51.0795 | 1.143
Water Power | (㎾) | 0 | 1.2356 | 2.2565 | 2.8728 | 2.3328 | 1.1656 | 0.027946
Shaft Power | (㎾) | 2.3828 | 3.108 | 3.663 | 3.9516 | 3.996 | 3.885 | 3.6704
Pump Eff. | (%) | 0 | 39.754 | 61.6033 | 72.6994 | 58.3792 | 30.0034 | 0.76139
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 13.05 | 14.43 | 16.58 | 17.54 | 17.72 | 17.31 | 16.59
Motor Input | (㎾) | 3.22 | 4.2 | 4.95 | 5.34 | 5.4 | 5.25 | 4.96
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 70 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 200 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.65
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 19 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | MARLEY | Turbin | 14 | 16
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-5032H |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-5033H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 48 | 80 | 109 | 123 | 141
Dis. Head | (m) | 273 | 235 | 190 | 120 | 80 | 5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.050483 | 0.14023 | 0.26032 | 0.33149 | 0.43561
Total Head | (m) | 273.7 | 235.7505 | 190.8402 | 120.9603 | 81.0315 | 6.1356
Water Power | (㎾) | 0 | 1.8445 | 2.4886 | 2.1491 | 1.6246 | 0.14101
Shaft Power | (㎾) | 2.4395 | 3.6593 | 3.9218 | 3.8754 | 3.7596 | 3.667
Pump Eff. | (%) | 0 | 50.4064 | 63.4551 | 55.4544 | 43.2116 | 3.8455
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.23 | 9.07 | 9.51 | 9.35 | 9.18 | 9
Motor Input | (㎾) | 3.16 | 4.74 | 5.08 | 5.02 | 4.87 | 4.75
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 70 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 200 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin | 19 | 16
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-5033H |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS4-7532H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 38 | 60 | 80 | 100 | 120 | 136
Dis. Head | (m) | 367 | 330 | 298 | 242 | 172 | 90 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.031639 | 0.078879 | 0.14023 | 0.21911 | 0.31552 | 0.40526
Total Head | (m) | 367.7 | 330.7316 | 298.7789 | 242.8402 | 172.9191 | 91.0155 | 4.1053
Water Power | (㎾) | 0 | 2.0486 | 2.9221 | 3.1666 | 2.8186 | 1.7803 | 0.091005
Shaft Power | (㎾) | 2.9822 | 4.3734 | 4.884 | 5.0986 | 5.1134 | 4.8174 | 4.4992
Pump Eff. | (%) | 0 | 46.8412 | 59.8292 | 62.108 | 55.1215 | 36.9549 | 2.0227
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 16.27 | 19.84 | 21.41 | 22.11 | 22.16 | 21.22 | 19.99
Motor Input | (㎾) | 4.03 | 5.91 | 6.6 | 6.89 | 6.91 | 6.51 | 6.08
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 230 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 26.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin | 14 | 16
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS4-7532H |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS4-7533H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 41 | 60 | 80 | 100 | 120 | 137
Dis. Head | (m) | 362 | 325 | 290 | 237 | 168 | 90 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.036832 | 0.078879 | 0.14023 | 0.21911 | 0.31552 | 0.41124
Total Head | (m) | 362.7 | 325.7368 | 290.7789 | 237.8402 | 168.9191 | 91.0155 | 4.1112
Water Power | (㎾) | 0 | 2.1769 | 2.8438 | 3.1014 | 2.7534 | 1.7803 | 0.091808
Shaft Power | (㎾) | 3.0266 | 4.5214 | 4.8766 | 5.0986 | 5.106 | 4.8766 | 4.514
Pump Eff. | (%) | 0 | 48.1466 | 58.3156 | 60.8292 | 53.9244 | 36.5062 | 2.0339
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 10.58 | 12.5 | 13.01 | 13.37 | 13.43 | 12.96 | 12.58
Motor Input | (㎾) | 4.09 | 6.11 | 6.59 | 6.89 | 6.9 | 6.59 | 6.1
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 230 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 16 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin | 14 | 16
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS4-7533H |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification