## Datasheet(PLS-1012)
Submersible Motor Pump Data Sheet
1 | Model | PLS-1012MP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 28 | m | Shaft | STS410
10 | Rated Capacity | 130 | ℓ/min | Shell | STS304
11 | Shut off Head | 49 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 55 | % | Sleeve | STS304
14 | Min. Flow | 80 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 170 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 40 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 9.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 393 | mm | Pump | 2.5 | kg
37 | Motor | 299 | mm | Motor | 10.9 | kg
38 | Total | 692 | mm | Total | 13.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (PLS-2012)
Submersible Motor Pump Data Sheet
1 | Model | PLS-2012MP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 47 | m | Shaft | STS410
10 | Rated Capacity | 130 | ℓ/min | Shell | STS304
11 | Shut off Head | 81 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 70 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 180 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 40 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 13.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 10 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 523 | mm | Pump | 3.5 | kg
37 | Motor | 385 | mm | Motor | 14.5 | kg
38 | Total | 908 | mm | Total | 18 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-2032)
Submersible Motor Pump Data Sheet
1 | Model | PLS-2032MP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 50 | m | Shaft | STS410
10 | Rated Capacity | 120 | ℓ/min | Shell | STS304
11 | Shut off Head | 81 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 70 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 180 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 40 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 8.1 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 10 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 523 | mm | Pump | 3.5 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 869 | mm | Total | 16.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-2033)
Submersible Motor Pump Data Sheet
1 | Model | PLS-2033MP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 50 | m | Shaft | STS410
10 | Rated Capacity | 120 | ℓ/min | Shell | STS304
11 | Shut off Head | 81 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 70 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 180 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 40 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 4.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 10 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 523 | mm | Pump | 3.5 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 869 | mm | Total | 16.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-3012)
Submersible Motor Pump Data Sheet
1 | Model | PLS-3012MP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 75 | m | Shaft | STS410
10 | Rated Capacity | 120 | ℓ/min | Shell | STS304
11 | Shut off Head | 113 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 70 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 180 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 40 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 17 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 14 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 656 | mm | Pump | 4.5 | kg
37 | Motor | 550 | mm | Motor | 20 | kg
38 | Total | 1206 | mm | Total | 24.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-3032)
Submersible Motor Pump Data Sheet
1 | Model | PLS-3032MP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 75 | m | Shaft | STS410
10 | Rated Capacity | 120 | ℓ/min | Shell | STS304
11 | Shut off Head | 113 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 70 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 180 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 40 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 14 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 656 | mm | Pump | 4.5 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 1156 | mm | Total | 21.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-3033)
Submersible Motor Pump Data Sheet
1 | Model | PLS-3033MP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 75 | m | Shaft | STS410
10 | Rated Capacity | 120 | ℓ/min | Shell | STS304
11 | Shut off Head | 113 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 70 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 180 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 40 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 6.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 14 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 656 | mm | Pump | 4.5 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 1156 | mm | Total | 21.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-5032M)
Submersible Motor Pump Data Sheet
1 | Model | PLS-5032M | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 110 | m | Shaft | STS410
10 | Rated Capacity | 120 | ℓ/min | Shell | STS304
11 | Shut off Head | 178 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 70 | ℓ/min | Head | HBsC1
15 | Max. Flow | 180 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 40 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 17.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 22 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 930 | mm | Pump | 8 | kg
37 | Motor | 602 | mm | Motor | 25 | kg
38 | Total | 1532 | mm | Total | 33 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-5033M)
Submersible Motor Pump Data Sheet
1 | Model | PLS-5033M | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 110 | m | Shaft | STS410
10 | Rated Capacity | 120 | ℓ/min | Shell | STS304
11 | Shut off Head | 178 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 70 | ℓ/min | Head | HBsC1
15 | Max. Flow | 180 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 40 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS410
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 22 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 930 | mm | Pump | 8 | kg
37 | Motor | 602 | mm | Motor | 25 | kg
38 | Total | 1532 | mm | Total | 33 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS4-7532M)
Submersible Motor Pump Data Sheet
1 | Model | PLS4-7532M | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 180 | m | Shaft | STS410
10 | Rated Capacity | 120 | ℓ/min | Shell | STS304
11 | Shut off Head | 270 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 70 | ℓ/min | Head | HBsC1
15 | Max. Flow | 180 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 40 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 26.4 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 34 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1350 | mm | Pump | 11 | kg
37 | Motor | 753 | mm | Motor | 31.8 | kg
38 | Total | 2103 | mm | Total | 42.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS4-7533M)
Submersible Motor Pump Data Sheet
1 | Model | PLS4-7533M | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 180 | m | Shaft | STS410
10 | Rated Capacity | 120 | ℓ/min | Shell | STS304
11 | Shut off Head | 270 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 60 | % | Middle Casing | Noryl
14 | Min. Flow | 70 | ℓ/min | Head | HBsC1
15 | Max. Flow | 180 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 40 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 16 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 34 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1350 | mm | Pump | 11 | kg
37 | Motor | 753 | mm | Motor | 31.8 | kg
38 | Total | 2103 | mm | Total | 42.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE |  | VOLTS | HZ
PLS-1012MP | 6 |  |  | 1 |  | 1 |  | 220 | 60
PLS-2012MP | 10 |  |  | 2 |  | 1 |  | 220 | 60
PLS-2032MP | 10 | 28 |  | 2 |  | 3 |  | 220 | 60
PLS-2033MP | 10 | 37 |  | 2 |  | 3 |  | 380 | 60
PLS-3012MP | 14 | 28 |  | 3 |  | 1 |  | 220 | 60
PLS-3032MP | 14 | 28 |  | 3 |  | 3 |  | 220 | 60
PLS-3033MP | 14 | 37 |  | 3 |  | 3 |  | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PLS-1012MP | 393 |  |  | 300 |  |  | 693
PLS-2012MP | 523 |  |  | 385 |  |  | 908
PLS-2032MP | 523 | 28 |  | 346 |  |  | 869
PLS-2033MP | 523 | 37 |  | 346 |  |  | 869
PLS-3012MP | 656 | 28 |  | 560 |  |  | 1216
PLS-3032MP | 656 | 28 |  | 500 |  |  | 1156
PLS-3033MP | 656 | 37 |  | 500 |  |  | 1156
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PLS-1012MP | 2.5 |  |  | 10.9 |  |  | 13.4
PLS-2012MP | 3.5 |  |  | 14.5 |  |  | 18
PLS-2032MP | 3.5 | 28 |  | 13.1 |  |  | 16.6
PLS-2033MP | 3.5 | 37 |  | 13.1 |  |  | 16.6
PLS-3012MP | 4.5 | 28 |  | 20 |  |  | 24.5
PLS-3032MP | 4.5 | 28 |  | 17 |  |  | 21.5
PLS-3033MP | 4.5 | 37 |  | 17 |  |  | 21.5
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
|  | TYPE |  |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PLS-MP Type
101mm
P.L
M.L
T.L
Cable Guard
Included

## Outline Drawing (2)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE | VOLTS | HZ
PLS-5032M | 22 |  |  | 5 |  | 3 | 220 | 60
PLS-5033M | 22 | 28 |  | 5 |  | 3 | 380 | 60
PLS4-7532M | 34 | 37 |  | 7.5 |  | 3 | 220 | 60
PLS4-7533M | 34 | 37 |  | 7.5 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PLS-5032M | 930 |  |  | 602 |  |  | 1532
PLS-5033M | 930 |  |  | 602 |  |  | 1532
PLS4-7532M | 1350 |  |  | 753 |  |  | 2103
PLS4-7533M | 1350 | 37 |  | 753 |  |  | 2103
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PLS-5032M | 8 |  |  | 25 |  |  | 33
PLS-5033M | 8 |  |  | 25 |  |  | 33
PLS4-7532M | 11 |  |  | 31.8 |  |  | 42.8
PLS4-7533M | 11 | 37 |  | 31.8 |  |  | 42.8
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE DIA. : 40mm
|  | TYPE |  |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PLS-M Type
101mm
P.L
M.L
T.L
Cable Guard
Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD,PUMP |  |  | POM + BRASS |  | 1
2 | STOP RING |  |  | STS304 |  | 1
3 | CHECK VALVE |  |  | NORYL + NBR |  | 1
4 | FIXING NUT |  |  | STS304 + NYLON |  | 1
5 | PLAIN WASHER |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | SLIDING BEARING |  |  | NBR |  | 1
8 | DIFFUSER |  |  | NORYL |  | Stages
9 | SLIDING BEARING |  |  | NBR |  | Stages
10 | UPTHRUST WASHER |  |  | STS304 |  | Stages
11 | MIDDLE CASING |  |  | NORYL |  | Stages
12 | IMPELLER |  |  | NORYL+STS304 |  | Stages
13 | IMPELLER GASKET |  |  | NBR |  | Stages
14 | MIDDLE SPACER |  |  | NORYL |  | 1~2
15 | SLEEVE |  |  | STS304 |  | 1~2
16 | SLIDING BEARING |  |  | NBR |  | 1~2
17 | SHELL |  |  | STS304 |  | 1
18 | LOWER SPACER |  |  | NORYL |  | 1
19 | SHAFT |  |  | STS410 |  | 1
20 | COUPLING |  |  | STS304 |  | 1
21 | SCREW |  |  | STS304 |  | 1
22 | STOPPER |  |  | STS304 |  | 1
23 | BASE |  |  | NORYL |  | 1
24 | SCREW |  |  | STS304 |  | 1
25 | CABLE GUARD |  |  | HD PE |  | 1
26 | STRAINER |  |  | STS304 |  | 1
27 | SCREW |  |  | STS304 |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
22
27
26
23
24
25
13
20
21
18
16
15
14
12
3
19
17
7
11
10
8
9
5
6
4
1
2
Sectional Drawing
of PLS-MP Type

## Sectional Drawing (2)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD,PUMP |  |  | BRASS |  | 1
2 | STOP RING |  |  | STS304 |  | 1
3 | CHECK VALVE |  |  | NORYL + NBR |  | 1
4 | FIXING NUT |  |  | STS304 + NYLON |  | 1
5 | PLAIN WASHER |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | SLIDING BEARING |  |  | NBR |  | 1
8 | SLEEVE |  |  | STS304 |  | 1
9 | DIFFUSER |  |  | NORYL |  | Stages
10 | SLIDING BEARING |  |  | NBR |  | Stages
11 | UPTHRUST WASHER |  |  | STS304 |  | Stages
12 | MIDDLE CASING |  |  | NORYL |  | Stages
13 | IMPELLER |  |  | NORYL+STS304 |  | Stages
14 | IMPELLER GASKET |  |  | NBR |  | Stages
15 | MIDDLE SPACER |  |  | NORYL |  | 1~2
16 | SLEEVE |  |  | STS304 |  | 1~2
17 | SLIDING BEARING |  |  | NBR |  | 1~2
18 | SHELL |  |  | STS304 |  | 1
19 | LOWER SPACER |  |  | NORYL |  | 1
20 | SHAFT |  |  | STS410 |  | 1
21 | COUPLING |  |  | STS304 |  | 1
22 | SCREW |  |  | STS304 |  | 1
23 | STOP RING |  |  | STS304 |  | 1
24 | BASE |  |  | BRASS |  | 1
25 | STRAINER |  |  | STS304 |  | 1
26 | SCREW |  |  | STS304 |  | 6
27 | CABLE GUARD |  |  | STS304 |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
13
25
24
26
21
23
22
12
19
14
20
18
27
7
11
16
17
15
9
10
8
6
5
4
3
2
1
Sectional Drawing
of PLS-M Type

## Test Report(PLS-1012)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.7 | 80.4 | 120 | 160.8 | 200.9 | 218.9
Dis. Head | (m) | 48 | 46 | 41 | 33 | 22 | 7.5 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014866 | 0.058014 | 0.12924 | 0.23206 | 0.36223 | 0.43004
Total Head | (m) | 49 | 47.0149 | 42.058 | 34.1292 | 23.2321 | 8.8622 | 3.43
Water Power | (㎾) | 0 | 0.3119 | 0.55118 | 0.66757 | 0.60892 | 0.29021 | 0.12239
Shaft Power | (㎾) | 0.60557 | 0.75022 | 0.87822 | 0.94251 | 0.91151 | 0.80532 | 0.75998
Pump Eff. | (%) | 0 | 41.5748 | 62.7609 | 70.8289 | 66.8034 | 36.0363 | 16.104
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.45 | 8.15 | 8.9 | 9.32 | 9.12 | 8.47 | 8.19
Motor Input | (㎾) | 1.055 | 1.307 | 1.53 | 1.642 | 1.588 | 1.403 | 1.324
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 120 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 30 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. | X1 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PLS-1012MP |  | Customer |  |  |  | 2 |  | 2007.10.01
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-2012)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.5 | 80.3 | 120.8 | 160.5 | 200.3 | 221.5
Dis. Head | (m) | 80.5 | 77 | 67.7 | 55 | 37.4 | 15 | 2.4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014721 | 0.05787 | 0.13096 | 0.23119 | 0.36007 | 0.44032
Total Head | (m) | 81.5 | 78.0147 | 68.7579 | 56.131 | 38.6312 | 16.3601 | 3.8403
Water Power | (㎾) | 0 | 0.51501 | 0.89996 | 1.1052 | 1.0106 | 0.53414 | 0.13865
Shaft Power | (㎾) | 1.0265 | 1.3106 | 1.5707 | 1.6952 | 1.6072 | 1.3953 | 1.2852
Pump Eff. | (%) | 0 | 39.2949 | 57.2969 | 65.197 | 62.8839 | 38.2822 | 10.7886
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.29 | 9.15 | 10.87 | 11.68 | 11 | 9.58 | 8.89
Motor Input | (㎾) | 1.492 | 1.905 | 2.283 | 2.464 | 2.336 | 2.028 | 1.868
Motor Eff. | (%) | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 120 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 50 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 13.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68.8 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PLS-2012MP |  | Customer |  |  |  | 2 |  | 2007.10.02
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-2032)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.3 | 81 | 120.4 | 160.4 | 200.5 | 222
Dis. Head | (m) | 81 | 77.4 | 68 | 56 | 37.8 | 15 | 2.4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014576 | 0.058883 | 0.1301 | 0.2309 | 0.36078 | 0.44231
Total Head | (m) | 82 | 78.4146 | 69.0589 | 57.1301 | 39.0309 | 16.3608 | 3.8423
Water Power | (㎾) | 0 | 0.5151 | 0.91178 | 1.1212 | 1.0205 | 0.53469 | 0.13904
Shaft Power | (㎾) | 0.9669 | 1.2396 | 1.4689 | 1.5664 | 1.4959 | 1.3122 | 1.2125
Pump Eff. | (%) | 0 | 41.5538 | 62.0745 | 71.5775 | 68.2173 | 40.7475 | 11.4667
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 5.06 | 5.84 | 6.54 | 6.84 | 6.58 | 6 | 5.67
Motor Input | (㎾) | 1.358 | 1.741 | 2.063 | 2.2 | 2.101 | 1.843 | 1.703
Motor Eff. | (%) | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 120 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 50 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 8.1 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 71.2 | Maker | FRANKLIN | Turbin | 0
Item No. |  |  | Serial No. | X1 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PLS-2032MP |  | Customer |  |  |  | 2 |  | 2007.10.05
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-2033)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.3 | 80.3 | 120.5 | 160.9 | 200.2 | 221.7
Dis. Head | (m) | 81 | 77.4 | 68 | 55.5 | 37.5 | 15 | 2.4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014576 | 0.05787 | 0.13031 | 0.23234 | 0.35971 | 0.44111
Total Head | (m) | 82 | 78.4146 | 69.0579 | 56.6303 | 38.7323 | 16.3597 | 3.8411
Water Power | (㎾) | 0 | 0.5151 | 0.90389 | 1.1123 | 1.0158 | 0.53386 | 0.13881
Shaft Power | (㎾) | 0.98269 | 1.2496 | 1.4693 | 1.5684 | 1.4895 | 1.313 | 1.2051
Pump Eff. | (%) | 0 | 41.2211 | 61.5177 | 70.9198 | 68.197 | 40.661 | 11.5182
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.38 | 3.76 | 4.13 | 4.31 | 4.17 | 3.86 | 3.67
Motor Input | (㎾) | 1.458 | 1.854 | 2.18 | 2.327 | 2.21 | 1.948 | 1.788
Motor Eff. | (%) | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 120 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 50 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 67.4 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. | X1 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PLS-2033MP |  | Customer |  |  |  | 2 |  | 2007.10.04
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-3012)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.4 | 80.4 | 120.5 | 160.3 | 200 | 221.6
Dis. Head | (m) | 115 | 110 | 97.6 | 79 | 52.5 | 20 | 2.4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014648 | 0.058014 | 0.13031 | 0.23061 | 0.35899 | 0.44072
Total Head | (m) | 116 | 111.0146 | 98.658 | 80.1303 | 53.7306 | 21.359 | 3.8407
Water Power | (㎾) | 0 | 0.73105 | 1.2929 | 1.5739 | 1.4039 | 0.6963 | 0.13873
Shaft Power | (㎾) | 1.4728 | 1.8788 | 2.2176 | 2.373 | 2.2561 | 1.9684 | 1.8025
Pump Eff. | (%) | 0 | 38.9107 | 58.3033 | 66.3245 | 62.2278 | 35.3741 | 7.6965
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 10.17 | 12.71 | 14.86 | 15.94 | 15.13 | 13.25 | 12.18
Motor Input | (㎾) | 2.104 | 2.684 | 3.168 | 3.39 | 3.223 | 2.812 | 2.575
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 120 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 75 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 17 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | Franklin | Turbin
Item No. |  |  | Serial No. | X1 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PLS-3012MP |  | Customer |  |  |  | 2 |  | 2007.10.09
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-3032)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.4 | 80.2 | 119.8 | 160.2 | 200.4 | 223.6
Dis. Head | (m) | 112.3 | 107 | 95 | 78 | 52.5 | 21 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014648 | 0.057726 | 0.12881 | 0.23033 | 0.36042 | 0.44871
Total Head | (m) | 113.3 | 108.0146 | 96.0577 | 79.1288 | 53.7303 | 22.3604 | 3.9487
Water Power | (㎾) | 0 | 0.7113 | 1.2557 | 1.5452 | 1.403 | 0.73041 | 0.14392
Shaft Power | (㎾) | 1.3557 | 1.7736 | 2.1104 | 2.2568 | 2.1565 | 1.8805 | 1.7246
Pump Eff. | (%) | 0 | 40.1039 | 59.503 | 68.4691 | 65.0618 | 38.841 | 8.345
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.78 | 8.06 | 9.09 | 9.61 | 9.26 | 8.42 | 7.95
Motor Input | (㎾) | 1.852 | 2.423 | 2.883 | 3.083 | 2.946 | 2.569 | 2.356
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 120 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 75 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 10.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. | X1 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PLS-3032MP |  | Customer |  |  |  | 2 |  | 07/10/10
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-3033)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.9 | 80.6 | 120.1 | 160.4 | 200.5 | 223.9
Dis. Head | (m) | 112.6 | 107.5 | 96 | 79 | 53 | 22.5 | 2.4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.015013 | 0.058303 | 0.12945 | 0.2309 | 0.36078 | 0.44991
Total Head | (m) | 113.6 | 108.515 | 97.0583 | 80.1295 | 54.2309 | 23.8608 | 3.8499
Water Power | (㎾) | 0 | 0.72344 | 1.2751 | 1.5686 | 1.4179 | 0.77981 | 0.14051
Shaft Power | (㎾) | 1.3849 | 1.8015 | 2.1323 | 2.2868 | 2.1814 | 1.9025 | 1.737
Pump Eff. | (%) | 0 | 40.1586 | 59.8004 | 68.5963 | 64.9997 | 40.9892 | 8.0888
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.46 | 5.02 | 5.59 | 5.82 | 5.65 | 5.17 | 4.93
Motor Input | (㎾) | 1.892 | 2.461 | 2.913 | 3.124 | 2.98 | 2.599 | 2.373
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 120 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 75 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. | X1 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PLS-3033MP |  | Customer |  |  |  | 2 |  | 07/10/11
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-5032M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.5 | 80 | 120.3 | 160.3 | 200 | 223.2
Dis. Head | (m) | 177 | 169 | 149.5 | 120 | 80 | 32.5 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014721 | 0.057438 | 0.12988 | 0.23061 | 0.35899 | 0.4471
Total Head | (m) | 178 | 170.0147 | 150.5574 | 121.1299 | 81.2306 | 33.859 | 3.9471
Water Power | (㎾) | 0 | 1.1224 | 1.9633 | 2.3752 | 2.1225 | 1.1038 | 0.1436
Shaft Power | (㎾) | 2.4164 | 3.1112 | 3.6145 | 3.8338 | 3.6361 | 3.1745 | 2.8564
Pump Eff. | (%) | 0 | 36.075 | 54.3164 | 61.9556 | 58.3717 | 34.7713 | 5.0274
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 11.27 | 13.1 | 14.56 | 15.3 | 14.66 | 13.24 | 12.35
Motor Input | (㎾) | 3.13 | 4.03 | 4.682 | 4.966 | 4.71 | 4.112 | 3.7
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 120 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 110 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 17.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. | X1 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PLS-5032M |  | Customer |  |  |  | 2 |  | 07/10/15
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-5033M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.5 | 80 | 120 | 160.3 | 200.6 | 223.9
Dis. Head | (m) | 178 | 171 | 151 | 123 | 82.5 | 33.5 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014721 | 0.057438 | 0.12924 | 0.23061 | 0.36114 | 0.44991
Total Head | (m) | 179 | 172.0147 | 152.0574 | 124.1292 | 83.7306 | 34.8611 | 3.9499
Water Power | (㎾) | 0 | 1.1356 | 1.9828 | 2.428 | 2.1878 | 1.1399 | 0.14415
Shaft Power | (㎾) | 2.4318 | 3.1559 | 3.6446 | 3.8832 | 3.6778 | 3.2046 | 2.9104
Pump Eff. | (%) | 0 | 35.9816 | 54.4044 | 62.5256 | 59.4862 | 35.5705 | 4.953
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.33 | 8.2 | 8.99 | 9.41 | 9.06 | 8.35 | 7.91
Motor Input | (㎾) | 3.15 | 4.088 | 4.721 | 5.03 | 4.764 | 4.151 | 3.77
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 120 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 110 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. | X1 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PLS-5033M |  | Customer |  |  |  | 2 |  | 07/10/16
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS4-7532M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.3 | 80.5 | 120 | 160 | 201 | 221.9
Dis. Head | (m) | 270 | 263 | 231 | 189 | 125 | 45 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014576 | 0.058158 | 0.12924 | 0.22975 | 0.36259 | 0.44191
Total Head | (m) | 271 | 264.0146 | 232.0582 | 190.1292 | 126.2298 | 46.3626 | 1.4419
Water Power | (㎾) | 0 | 1.7343 | 3.045 | 3.7189 | 3.2921 | 1.519 | 0.052153
Shaft Power | (㎾) | 3.3818 | 4.4696 | 5.2022 | 5.4982 | 5.217 | 4.5362 | 4.1366
Pump Eff. | (%) | 0 | 38.8018 | 58.532 | 67.639 | 63.1028 | 33.4857 | 1.2608
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 10.29 | 11.88 | 13.12 | 13.66 | 13.24 | 12 | 11.32
Motor Input | (㎾) | 4.57 | 6.04 | 7.03 | 7.43 | 7.05 | 6.13 | 5.59
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 120 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 180 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 16.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. | X1 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PLS4-7533M |  | Customer |  |  |  | 2 |  | 07/10/12
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS4-7533M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.3 | 80.5 | 120 | 160 | 201 | 221.9
Dis. Head | (m) | 270 | 263 | 231 | 189 | 125 | 45 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014576 | 0.058158 | 0.12924 | 0.22975 | 0.36259 | 0.44191
Total Head | (m) | 271 | 264.0146 | 232.0582 | 190.1292 | 126.2298 | 46.3626 | 1.4419
Water Power | (㎾) | 0 | 1.7343 | 3.045 | 3.7189 | 3.2921 | 1.519 | 0.052153
Shaft Power | (㎾) | 3.3818 | 4.4696 | 5.2022 | 5.4982 | 5.217 | 4.5362 | 4.1366
Pump Eff. | (%) | 0 | 38.8018 | 58.532 | 67.639 | 63.1028 | 33.4857 | 1.2608
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 10.29 | 11.88 | 13.12 | 13.66 | 13.24 | 12 | 11.32
Motor Input | (㎾) | 4.57 | 6.04 | 7.03 | 7.43 | 7.05 | 6.13 | 5.59
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 120 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 180 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 16.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. | X1 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PLS4-7533M |  | Customer |  |  |  | 2 |  | 07/10/12
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification