## Datasheet(PLS-2012QP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-2012QP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 32 | m | Shaft | STS410
10 | Rated Capacity | 180 | ℓ/min | Shell | STS304
11 | Shut off Head | 50 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Liner Ring | STS304
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | POM+Brass
15 | Max. Flow | 250 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 50 | mm | Coupling | STS304
17 | Out Dia. | 104mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 13.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 550 | mm | Pump | 5.5 | kg
37 | Motor | 385 | mm | Motor | 14.5 | kg
38 | Total | 935 | mm | Total | 20 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-2033QP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-2033QP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 35 | m | Shaft | STS410
10 | Rated Capacity | 180 | ℓ/min | Shell | STS304
11 | Shut off Head | 50 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Liner Ring | STS304
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | POM+Brass
15 | Max. Flow | 250 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 50 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 4.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 550 | mm | Pump | 5.5 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 896 | mm | Total | 18.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-3012QP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-3012QP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 45 | m | Shaft | STS410
10 | Rated Capacity | 180 | ℓ/min | Shell | STS304
11 | Shut off Head | 65 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Liner Ring | STS304
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | POM+BRASS
15 | Max. Flow | 250 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 50 | mm | Coupling | STS304
17 | Out Dia. | 104mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 17 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 830 | mm | Pump | 6.5 | kg
37 | Motor | 550 | mm | Motor | 20 | kg
38 | Total | 1380 | mm | Total | 26.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-3033QP)
Submersible Motor Pump Data Sheet
1 | Model | PLS-3033QP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 45 | m | Shaft | STS410
10 | Rated Capacity | 180 | ℓ/min | Shell | STS304
11 | Shut off Head | 65 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Liner Ring | STS304
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | POM+BRASS
15 | Max. Flow | 250 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 50 | mm | Coupling | STS304
17 | Out Dia. | 104mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 6.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 830 | mm | Pump | 6.5 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 1330 | mm | Total | 23.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-5033Q)
Submersible Motor Pump Data Sheet
1 | Model | PLS-5033Q | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 70 | m | Shaft | STS410
10 | Rated Capacity | 180 | ℓ/min | Shell | STS304
11 | Shut off Head | 110 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Liner Ring | STS304
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | HBsC1
15 | Max. Flow | 250 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 50 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 945 | mm | Pump | 9 | kg
37 | Motor | 602 | mm | Motor | 25 | kg
38 | Total | 1547 | mm | Total | 34 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS4-7533Q)
Submersible Motor Pump Data Sheet
1 | Model | PLS4-7533Q | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 110 | m | Shaft | STS410
10 | Rated Capacity | 180 | ℓ/min | Shell | STS304
11 | Shut off Head | 160 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Liner Ring | STS304
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | HBsC1
15 | Max. Flow | 250 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 50 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 16 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 19 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1275 | mm | Pump | 11 | kg
37 | Motor | 753 | mm | Motor | 31.8 | kg
38 | Total | 2028 | mm | Total | 42.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing(PLS-QP)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE |  | VOLTS | HZ
PLS-2012QP | 6 |  |  | 2 |  | 1 |  | 220 | 60
PLS-2033QP | 6 |  |  | 2 |  | 3 |  | 380 | 60
PLS-3012QP | 8 |  |  | 3 |  | 1 |  | 220 | 60
PLS-3033QP | 8 | 28 |  | 3 |  | 3 |  | 380 | 60
PLS-5033QP | 13 | 28 |  | 5 |  | 3 |  | 380 | 60
PLS4-7533Q | 19 |  |  | 7.5 |  | 3 |  | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PLS-2012QP | 550 |  |  | 385 |  |  | 935
PLS-2033QP | 550 |  |  | 346 |  |  | 896
PLS-3012QP | 830 |  |  | 560 |  |  | 1390
PLS-3033QP | 830 |  |  | 500 |  |  | 1330
PLS-5033QP | 1110 |  |  | 602 |  |  | 1712
PLS4-7533Q | 1275 |  |  | 753 |  |  | 2028
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PLS-2012QP | 5.5 |  |  | 14.5 |  |  | 20
PLS-2033QP | 5.5 |  |  | 13.1 |  |  | 18.6
PLS-3012QP | 6.5 |  |  | 20 |  |  | 26.5
PLS-3033QP | 6.5 | 28 |  | 17 |  |  | 23.5
PLS-5033QP | 8 | 28 |  | 25 |  |  | 33
PLS4-7533Q | 11 |  |  | 31.8 |  |  | 42.8
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 2" (50mm)
|  | TYPE |  |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PLS-QP MODEL

## Sectional Drawing(PLS-QP)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD |  |  | POM+Brass |  | 1
2 | STOPPER |  |  | STS304 |  | 1
3 | CHECK VALVE |  |  | NORYL + NBR |  | 1
4 | FIXING NUT |  |  | STS304 + NYLON |  | 1
5 | PLAIN WASHER |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | SLIDING BEARING |  |  | NBR |  | 1
8 | SLEEVE |  |  | STS304 |  | 1
9 | DIFFUSER COVER |  |  | NORYL+STS304 |  | Stages
10 | DIFLECTOR |  |  | NORYL |  | Stages
11 | DIFFUSER BODY |  |  | NORYL |  | Stages
12 | SLIDING BEARING |  |  | NBR |  | Stages
13 | SLEEVE |  |  | STS304 |  | Stages
14 | UPTHRUST WASHER |  |  | STS304 |  | Stages
15 | IMPELLER |  |  | NORYL |  | Stages
16 | SHAFT |  |  | STS410 |  | 1
17 | SHELL |  |  | STS304 |  | 1
18 | DIFFUSER COVER |  |  | NORYL |  | 1
19 | LOWER SPACER |  |  | NORYL |  | 1
20 | COUPLING |  |  | STS304 |  | 1
21 | SCREW |  |  | STS304 |  | 1
22 | STOPPER |  |  | STS304 |  | 1
23 | STRAINER |  |  | STS304 |  | 1
24 | BASE |  |  | BRASS |  | 1
25 | SCREW |  |  | STS304 |  | 1
26 | CABLE GUARD |  |  | PVC |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PLS-QP Model

## Test Report(PLS-2012Q)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 120 | 180 | 240 | 325
Dis. Head | (m) | 51.3 | 49.5 | 42.5 | 36 | 25.5 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.052935 | 0.1191 | 0.21174 | 0.38828
Total Head | (m) | 52 | 50.2092 | 43.2529 | 36.8191 | 26.4117 | 5.0883
Water Power | (㎾) | 0 | 0.4092 | 0.84603 | 1.0803 | 1.0332 | 0.26955
Shaft Power | (㎾) | 1.1077 | 1.3141 | 1.5893 | 1.8645 | 1.9126 | 1.8576
Pump Eff. | (%) | 0 | 31.14 | 53.2334 | 57.9396 | 54.021 | 14.5107
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.4 | 8.5 | 10.1 | 12.9 | 13.11 | 12.9
Motor Input | (㎾) | 1.61 | 1.91 | 2.31 | 2.71 | 2.78 | 2.7
Motor Eff. | (%) | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 180 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 32 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.7
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 13.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68.8 | Maker | FRANKLIN | Turbin | 13 | 17
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-2012Q |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-2033Q)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 60 | 120 | 180 | 240 | 323
Dis. Head | (m) | 50.3 | 47.5 | 42 | 36 | 26 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013234 | 0.052935 | 0.1191 | 0.21174 | 0.38352
Total Head | (m) | 51 | 48.2132 | 42.7529 | 36.8191 | 26.9117 | 5.0835
Water Power | (㎾) | 0 | 0.47153 | 0.83625 | 1.0803 | 1.0528 | 0.26764
Shaft Power | (㎾) | 1.1121 | 1.3952 | 1.5569 | 1.7187 | 1.7457 | 1.7052
Pump Eff. | (%) | 0 | 33.7967 | 53.711 | 62.854 | 60.3088 | 15.6955
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.61 | 4.02 | 4.41 | 4.72 | 4.77 | 4.71
Motor Input | (㎾) | 1.65 | 2.07 | 2.31 | 2.55 | 2.59 | 2.53
Motor Eff. | (%) | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 180 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 32 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 5.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 67.4 | Maker | MARLEY | Turbin | 20 | 17
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-2033Q |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-3012Q)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 60 | 120 | 180 | 240 | 325
Dis. Head | (m) | 69 | 64.5 | 57.5 | 49 | 34 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013234 | 0.052935 | 0.1191 | 0.21174 | 0.38828
Total Head | (m) | 69.7 | 65.2132 | 58.2529 | 49.8191 | 34.9117 | 5.0883
Water Power | (㎾) | 0 | 0.63779 | 1.1394 | 1.4617 | 1.3657 | 0.26955
Shaft Power | (㎾) | 1.4266 | 1.8396 | 2.1469 | 2.401 | 2.4227 | 2.3618
Pump Eff. | (%) | 0 | 34.6698 | 53.0731 | 60.8785 | 56.3729 | 11.413
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 9.87 | 12.64 | 14.65 | 16.4 | 16.7 | 16.31
Motor Input | (㎾) | 2.038 | 2.628 | 3.067 | 3.43 | 3.461 | 3.374
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 180 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 45 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.7
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 17 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | FRANKLIN | Turbin | 28 | 25
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-3012Q |  | Customer |  |  |  | 3
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Reprot(PLS-3033Q)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 60 | 120 | 180 | 240 | 318
Dis. Head | (m) | 69.5 | 64.5 | 57.6 | 49 | 33.7 | 3.7
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013234 | 0.052935 | 0.1191 | 0.21174 | 0.37173
Total Head | (m) | 70.2 | 65.2132 | 58.3529 | 49.8191 | 34.6117 | 4.7717
Water Power | (㎾) | 0 | 0.63779 | 1.1414 | 1.4617 | 1.354 | 0.24734
Shaft Power | (㎾) | 1.4904 | 1.8864 | 2.1744 | 2.3904 | 2.4336 | 2.304
Pump Eff. | (%) | 0 | 33.8097 | 52.4919 | 61.1484 | 55.6382 | 10.7352
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 5.72 | 6.26 | 6.67 | 6.94 | 6.96 | 6.83
Motor Input | (㎾) | 2.07 | 2.62 | 3.02 | 3.32 | 3.38 | 3.2
Motor Eff. | (%) | 72 | 72 | 72 | 72 | 72 | 72
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 180 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 45 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 7.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 72 | Maker | MARLEY | Turbin | 27 | 24
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-3033Q |  | Customer |  |  |  | 3
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-5033Q)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 60 | 120 | 180 | 240 | 333
Dis. Head | (m) | 113 | 108 | 93 | 77 | 54 | 5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013234 | 0.052935 | 0.1191 | 0.21174 | 0.40763
Total Head | (m) | 113.75 | 108.7632 | 93.8029 | 77.8691 | 54.9617 | 6.1576
Water Power | (㎾) | 0 | 1.0637 | 1.8348 | 2.2847 | 2.1501 | 0.33423
Shaft Power | (㎾) | 2.2743 | 3.0107 | 3.3645 | 3.6966 | 3.7039 | 3.4945
Pump Eff. | (%) | 0 | 35.3303 | 54.5333 | 61.8042 | 58.0503 | 9.5645
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.8 | 8.85 | 9.46 | 10.01 | 10.04 | 9.65
Motor Input | (㎾) | 3.15 | 4.17 | 4.66 | 5.12 | 5.13 | 4.84
Motor Eff. | (%) | 72.2 | 72.2 | 72.2 | 72.2 | 72.2 | 72.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 180 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 70 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.75
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 72.2 | Maker | FRANKLIN | Turbin | 28 | 24
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-5033Q |  | Customer |  |  |  | 2 |  | 00/12/4
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS4-7533Q)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 70 | 170 | 240 | 300 | 327
Dis. Head | (m) | 163 | 155 | 119.3 | 80 | 35 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.018013 | 0.10624 | 0.21174 | 0.33084 | 0.39307
Total Head | (m) | 163.8 | 155.818 | 120.2062 | 81.0117 | 36.1308 | 1.1931
Water Power | (㎾) | 0 | 1.7779 | 3.3309 | 3.1692 | 1.7668 | 0.063592
Shaft Power | (㎾) | 3.1672 | 4.4326 | 5.3724 | 5.3946 | 5.1356 | 5.0394
Pump Eff. | (%) | 0 | 40.1093 | 62.0005 | 58.7473 | 34.403 | 1.2619
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 10.73 | 12.6 | 14.14 | 14.1 | 13.7 | 13.53
Motor Input | (㎾) | 4.28 | 5.99 | 7.26 | 7.29 | 6.94 | 6.81
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 190 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 105 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.8
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 16 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin | 30 | 28
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS4-7533Q |  | Customer |  |  |  | 3
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification