## Datasheet(PLS-7533H)
Submersible Motor Pump Data Sheet
1 | Model | PLS-7533H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 110 | m | Shaft | STS410
10 | Rated Capacity | 160 | ℓ/min | Shell | STS304
11 | Shut off Head | 155 | m | Impeller / Diffuser | Noryl
12 | Speed | 2875 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 50 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | HBsC1
15 | Max. Flow | 250 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 65 | mm | Coupling | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 50 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 14.9 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1500 lbs |  | Castings | Gray Iron
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 11 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 797 | mm | Pump | 23 | kg
37 | Motor | 614 | mm | Motor | 43 | kg
38 | Total | 1411 | mm | Total | 66 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-10033H)
Submersible Motor Pump Data Sheet
1 | Model | PLS-10033H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 140 | m | Shaft | STS410
10 | Rated Capacity | 200 | ℓ/min | Shell | STS304
11 | Shut off Head | 195 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 55 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | HBsC1
15 | Max. Flow | 250 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 65 | mm | Coupling | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 32.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 10 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 747 | mm | Pump | 22 | kg
37 | Motor | 646 | mm | Motor | 47.6 | kg
38 | Total | 1393 | mm | Total | 69.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-15033H)
Submersible Motor Pump Data Sheet
1 | Model | PLS-15033H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 210 | m | Shaft | STS410
10 | Rated Capacity | 200 | ℓ/min | Shell | STS304
11 | Shut off Head | 290 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 55 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | HBsC1
15 | Max. Flow | 250 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 65 | mm | Coupling | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 28.7 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 15 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 997 | mm | Pump | 26 | kg
37 | Motor | 711 | mm | Motor | 54.4 | kg
38 | Total | 1708 | mm | Total | 80.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-20033H)
Submersible Motor Pump Data Sheet
1 | Model | PLS-20033H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 280 | m | Shaft | STS410
10 | Rated Capacity | 200 | ℓ/min | Shell | STS304
11 | Shut off Head | 390 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 55 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | HBsC1
15 | Max. Flow | 250 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 65 | mm | Coupling | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 15 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 36.7 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 20 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1247 | mm | Pump | 32 | kg
37 | Motor | 776 | mm | Motor | 61.2 | kg
38 | Total | 2023 | mm | Total | 93.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-25033H)
Submersible Motor Pump Data Sheet
1 | Model | PLS-25033H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 320 | m | Shaft | STS410
10 | Rated Capacity | 200 | ℓ/min | Shell | STS304
11 | Shut off Head | 450 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 48 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | HBsC1
15 | Max. Flow | 250 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 65 | mm | Coupling | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 19 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 45.4 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 24 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1447 | mm | Pump | 37 | kg
37 | Motor | 842 | mm | Motor | 67.1 | kg
38 | Total | 2289 | mm | Total | 104.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE | VOLTS | HZ
PLS-7532H | 8 |  |  | 7.5 |  | 3 | 220 | 60
PLS-7533H | 8 |  |  | 7.5 |  | 3 | 380 | 60
PLS-10032H | 10 |  |  | 10 |  | 3 | 220 | 60
PLS-10033H | 10 | 28 |  | 10 |  | 3 | 380 | 60
PLS-15033H | 15 | 28 |  | 15 |  | 3 | 380 | 60
PLS-20033H | 20 | 37 |  | 20 |  | 3 | 380 | 60
PLS-25033H | 24 |  |  | 25 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PLS-7532/33H | 648 |  |  | 614 |  |  | 1262
PLS-10032/33H | 747 |  |  | 646 |  |  | 1393
PLS-15033H | 997 |  |  | 711 |  |  | 1708
PLS-20033H | 1247 |  |  | 776 |  |  | 2023
PLS-25033H | 1447 |  |  | 842 |  |  | 2289
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PLS-7532/33H | 20 |  |  | 43 |  |  | 63
PLS-10032/33H | 22 |  |  | 48 |  |  | 70
PLS-15033H | 26 |  |  | 54 |  |  | 80
PLS-20033H | 32 |  |  | 61 |  |  | 93
PLS-25033H | 37 |  |  | 67.1 |  |  | 104.1
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 2½" (65mm)
|  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PLS-6INCH MODEL
145mm
P.L
M.L
T.L
Cable Guard Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD |  |  | BRASS |  | 1
2 | HEX BOLT |  |  | STS304 |  | 1~2
3 | SPRING WASHER |  |  | STS304 |  | 1~2
4 | PLAIN WASHER |  |  | NORYL |  | 1~2
5 | SLIDING BEARING |  |  | STS410 |  | 1
6 | SLEEVE |  |  | NBR |  | 2
7 | SLIDING BEARING |  |  | NORYL+STS304 |  | Stages
8 | DIFFUSER COVER |  |  | NORYL |  | Stages
9 | DIFFUSER BODY |  |  | NORYL |  | Stages
10 | SLEEVE |  |  | NBR |  | Stages
11 | UPTHRUST WASHER |  |  | NORYL |  | Stages
12 | IMPELLER |  |  | NORYL |  | Stages
13 | SLEEVE |  |  | STS304 |  | 1
14 | SHAFT |  |  | STS410 |  | 1
15 | STOPPER |  |  | STS304 |  | 1
16 | COUPLING |  |  | STS304 |  | 1
17 | SLEEVE |  |  | STS304 |  | 1
18 | BASE |  |  | BRASS |  | 1
19 | SHELL |  |  | STS304 |  | 1
20 | CABLE GUARD |  |  | STS304 |  | 1
21 | SCREW |  |  | STS304 |  | 8
22 | STRAINER |  |  | STS304 |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PLS-6INCH H TYPE
18
7
11
16
17
15
9
10
8
6
5
4
3
2
1
12
13
14
19
20
21
22

## Test Report(PLS-7533H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 80 | 100 | 150 | 190 | 250 | 300 | 320
Dis. Head | (m) | 153 | 145 | 143 | 130 | 116 | 88 | 56 | 20
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0082373 | 0.012871 | 0.028959 | 0.046464 | 0.080443 | 0.11584 | 0.1318
Total Head | (m) | 154.7 | 146.7082 | 144.7129 | 131.729 | 117.7465 | 89.7804 | 57.8158 | 21.8318
Water Power | (㎾) | 0 | 1.9131 | 2.3588 | 3.2208 | 3.6466 | 3.6586 | 2.8272 | 1.1387
Shaft Power | (㎾) | 3.8799 | 5.0762 | 5.2729 | 5.8868 | 6.1858 | 6.296 | 6.0363 | 5.5798
Pump Eff. | (%) | 0 | 37.6875 | 44.7348 | 54.7122 | 58.9511 | 58.1092 | 46.8366 | 20.4083
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 10.68 | 12.61 | 12.82 | 13.91 | 14.56 | 14.57 | 14.16 | 13.4
Motor Input | (㎾) | 4.93 | 6.45 | 6.7 | 7.48 | 7.86 | 8 | 7.67 | 7.09
Motor Eff. | (%) | 78.7 | 78.7 | 78.7 | 78.7 | 78.7 | 78.7 | 78.7 | 78.7
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 160 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 110 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 14.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78.7 | Maker | FRANKLIN | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-7533H |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-10033H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 83 | 142 | 200 | 280 | 323
Dis. Head | (m) | 197 | 187 | 175 | 152 | 98 | 42
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0038642 | 0.01131 | 0.022437 | 0.043976 | 0.05852
Total Head | (m) | 198.6 | 188.6039 | 176.6113 | 153.6224 | 99.644 | 43.6585
Water Power | (㎾) | 0 | 2.5516 | 4.0878 | 5.0081 | 4.5478 | 2.2986
Shaft Power | (㎾) | 4.797 | 6.3492 | 7.2774 | 7.9014 | 7.9326 | 7.3164
Pump Eff. | (%) | 0 | 40.1881 | 56.1718 | 63.3823 | 57.3299 | 31.4168
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 13.34 | 15.86 | 17.52 | 18.66 | 18.69 | 17.56
Motor Input | (㎾) | 6.15 | 8.14 | 9.33 | 10.13 | 10.17 | 9.38
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 140 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 1.6
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | FRANKLIN | Turbin | 17 | 22
Item No. |  |  | Serial No. |  | Inspector | P.T.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-10033H |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-15033H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 100 | 150 | 200 | 250 | 300
Dis. Head | (m) | 296 | 272 | 250 | 217 | 178 | 120
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.012871 | 0.028959 | 0.051483 | 0.080443 | 0.11584
Total Head | (m) | 297.6 | 273.6129 | 251.629 | 218.6515 | 179.6804 | 121.7158
Water Power | (㎾) | 0 | 4.4599 | 6.1523 | 7.128 | 7.322 | 5.9519
Shaft Power | (㎾) | 7.6511 | 10.1854 | 11.3162 | 11.9819 | 12.1343 | 11.7573
Pump Eff. | (%) | 0 | 43.7871 | 54.3673 | 59.4901 | 60.3414 | 50.623
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 19.9 | 23.89 | 25.93 | 27.06 | 27.44 | 26.62
Motor Input | (㎾) | 9.54 | 12.7 | 14.11 | 14.94 | 15.13 | 14.66
Motor Eff. | (%) | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 210 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 1.6
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 28.7 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80.2 | Maker | FRANKLIN | Turbin | 12 | 22
Item No. |  |  | Serial No. |  | Inspector | P.T.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-15033H |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-20033H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 83 | 142 | 200 | 280 | 325
Dis. Head | (m) | 394 | 367 | 336 | 286 | 186 | 90
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0038642 | 0.01131 | 0.022437 | 0.043976 | 0.059247
Total Head | (m) | 395.6 | 368.6039 | 337.6113 | 287.6224 | 187.644 | 91.6592
Water Power | (㎾) | 0 | 4.9868 | 7.8144 | 9.3765 | 8.5641 | 4.8556
Shaft Power | (㎾) | 10.7141 | 13.211 | 15.0226 | 16.1486 | 16.0834 | 14.7125
Pump Eff. | (%) | 0 | 37.7475 | 52.0174 | 58.0637 | 53.248 | 33.0036
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 26.24 | 30.76 | 33.92 | 35.94 | 35.89 | 33.35
Motor Input | (㎾) | 13.13 | 16.19 | 18.41 | 19.79 | 19.71 | 18.03
Motor Eff. | (%) | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 15 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 280 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 1.6
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 36.7 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 81.6 | Maker | FRANKLIN | Turbin | 14 | 20
Item No. |  |  | Serial No. |  | Inspector | P.T.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-20033H |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-25033H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 80 | 100 | 150 | 200 | 250 | 300 | 327
Dis. Head | (m) | 476 | 440 | 429 | 395 | 343 | 275 | 185 | 50
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0082373 | 0.012871 | 0.028959 | 0.051483 | 0.080443 | 0.11584 | 0.13763
Total Head | (m) | 477.7 | 441.7082 | 430.7129 | 396.729 | 344.7515 | 276.7804 | 186.8158 | 51.8376
Water Power | (㎾) | 0 | 5.7599 | 7.0206 | 9.7 | 11.2389 | 11.2788 | 9.1353 | 2.763
Shaft Power | (㎾) | 12.8412 | 15.99 | 16.646 | 18.4254 | 19.434 | 19.6718 | 18.9502 | 17.3348
Pump Eff. | (%) | 0 | 36.0217 | 42.176 | 52.6448 | 57.8311 | 57.3349 | 48.2068 | 15.939
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 31.96 | 36.73 | 37.93 | 40.87 | 42.85 | 43.27 | 41.95 | 38.81
Motor Input | (㎾) | 15.66 | 19.5 | 20.3 | 22.47 | 23.7 | 23.99 | 23.11 | 21.14
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 18.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 320 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 1.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 45.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | FRANKLIN | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-25033H |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification