## Datasheet(PLS-7533M)
Submersible Motor Pump Data Sheet
1 | Model | PLS-7533M | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 70 | m | Shaft | STS410
10 | Rated Capacity | 280 | ℓ/min | Shell | STS304
11 | Shut off Head | 100 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 50 | % | Sleeve | STS304
14 | Min. Flow | 150 | ℓ/min | Head | HBsC1
15 | Max. Flow | 350 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 65 | mm | Coupling | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 14.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 648 | mm | Pump | 19 | kg
37 | Motor | 614 | mm | Motor | 43 | kg
38 | Total | 1262 | mm | Total | 62 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-10033M)
Submersible Motor Pump Data Sheet
1 | Model | PLS-10033M | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 100 | m | Shaft | STS410
10 | Rated Capacity | 300 | ℓ/min | Shell | STS304
11 | Shut off Head | 130 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 55 | % | Sleeve | STS304
14 | Min. Flow | 200 | ℓ/min | Head | HBsC1
15 | Max. Flow | 400 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 65 | mm | Coupling | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 19.5 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 747 | mm | Pump | 20 | kg
37 | Motor | 646 | mm | Motor | 48 | kg
38 | Total | 1393 | mm | Total | 68 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-15033M)
Submersible Motor Pump Data Sheet
1 | Model | PLS-15033M | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 150 | m | Shaft | STS410
10 | Rated Capacity | 300 | ℓ/min | Shell | STS304
11 | Shut off Head | 200 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 55 | % | Sleeve | STS304
14 | Min. Flow | 180 | ℓ/min | Head | HBsC1
15 | Max. Flow | 400 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 65 | mm | Coupling | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 28.7 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 12 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 913 | mm | Pump | 24 | kg
37 | Motor | 711 | mm | Motor | 54 | kg
38 | Total | 1624 | mm | Total | 78 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-20033M)
Submersible Motor Pump Data Sheet
1 | Model | PLS-20033M | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 200 | m | Shaft | STS410
10 | Rated Capacity | 300 | ℓ/min | Shell | STS304
11 | Shut off Head | 265 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 55 | % | Sleeve | STS304
14 | Min. Flow | 180 | ℓ/min | Head | HBsC1
15 | Max. Flow | 400 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 65 | mm | Coupling | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 15 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 36.7 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 16 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1077 | mm | Pump | 28 | kg
37 | Motor | 776 | mm | Motor | 61 | kg
38 | Total | 1853 | mm | Total | 89 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-25033M)
Submersible Motor Pump Data Sheet
1 | Model | PLS-25033M | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 250 | m | Shaft | STS410
10 | Rated Capacity | 300 | ℓ/min | Shell | STS304
11 | Shut off Head | 330 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 48 | % | Sleeve | STS304
14 | Min. Flow | 200 | ℓ/min | Head | HBsC1
15 | Max. Flow | 400 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 65 | mm | Coupling | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 19 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 45.4 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 20 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1247 | mm | Pump | 32 | kg
37 | Motor | 842 | mm | Motor | 67.1 | kg
38 | Total | 2089 | mm | Total | 99.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PLS-30033M)
Submersible Motor Pump Data Sheet
1 | Model | PLS-30033M | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 270 | m | Shaft | STS410
10 | Rated Capacity | 270 | ℓ/min | Shell | STS304
11 | Shut off Head | 380 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Middle Casing | Noryl
13 | Rated Efficiency | 48 | % | Sleeve | STS304
14 | Min. Flow | 150 | ℓ/min | Head | HBsC1
15 | Max. Flow | 350 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 65 | mm | Coupling | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 55.4 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 24 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1447 | mm | Pump | 37 | kg
37 | Motor | 907 | mm | Motor | 73.5 | kg
38 | Total | 2354 | mm | Total | 110.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE | VOLTS | HZ
PLS-7533M | 6 |  |  | 7.5 |  | 3 | 380 | 60
PLS-10033M | 8 | 28 |  | 10 |  | 3 | 380 | 60
PLS-15033M | 12 | 28 |  | 15 |  | 3 | 380 | 60
PLS-20033M | 16 | 37 |  | 20 |  | 3 | 380 | 60
PLS-25033M | 20 |  |  | 25 |  | 3 | 380 | 60
PLS-30033M | 24 |  |  | 30 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PLS-7533M | 648 |  |  | 614 |  |  | 1262
PLS-10033M | 747 |  |  | 646 |  |  | 1393
PLS-15033M | 913 |  |  | 711 |  |  | 1624
PLS-20033M | 1077 |  |  | 776 |  |  | 1853
PLS-25033M | 1247 |  |  | 842 |  |  | 2089
PLS-30033M | 1447 |  |  | 907 |  |  | 2354
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PLS-7533M | 19 |  |  | 43 |  |  | 62
PLS-10033M | 20 |  |  | 48 |  |  | 68
PLS-15033M | 24 |  |  | 54 |  |  | 78
PLS-20033M | 28 |  |  | 61 |  |  | 89
PLS-25033M | 32 |  |  | 67.1 |  |  | 99.1
PLS-30033M | 37 |  |  | 73.5 |  |  | 110.5
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 2½" (65mm)
|  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PLS-6INCH MODEL
145mm
P.L
M.L
T.L
Cable Guard Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | BASE |  |  | BRASS |  | 1
2 | SLEEVE |  |  | STS304 |  | 1
3 | COUPLING |  |  | STS304 |  | 1
4 | STOPPER |  |  | STS304 |  | 1
5 | SHAFT |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | IMPELLER |  |  | NBR |  | Stages
8 | UPTHRUST WASHER |  |  | NORYL |  | Stages
9 | SLEEVE |  |  | NBR |  | Stages
10 | DIFFUSER BODY |  |  | STS304 |  | Stages
11 | DIFFUSR COVER |  |  | NORYL |  | Stages
12 | SLIDING BEARING |  |  | NORYL+STS304 |  | Stages
13 | SLEEVE |  |  | NBR |  | 2
14 | PLAIN WASHER |  |  | NORYL |  | 1~2
15 | SPRING WASHER |  |  | STS304 |  | 1~2
16 | HEX BOLT |  |  | NBR |  | 1~2
17 | SHELL |  |  | STS304 |  | 1
18 | HEAD |  |  | BRASS |  | 1
19 | SLIDING BEARING |  |  | STS410 |  | 1
20 | STRAINER |  |  | STS304 |  | 1
21 | CABLE GUARD |  |  | STS304 |  | 1
22 | SCREW |  |  | STS304 |  | 8
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | BASE |  |  | BRASS |  | 1
2 | SLEEVE |  |  | STS304 |  | 1
3 | COUPLING |  |  | STS304 |  | 1
4 | STOPPER |  |  | STS304 |  | 1
5 | SHAFT |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | IMPELLER |  |  | NBR |  | Stages
8 | UPTHRUST WASHER |  |  | NORYL |  | Stages
9 | SLEEVE |  |  | NBR |  | Stages
10 | DIFFUSER BODY |  |  | STS304 |  | Stages
11 | DIFFUSR COVER |  |  | NORYL |  | Stages
12 | SLIDING BEARING |  |  | NORYL+STS304 |  | Stages
13 | SLEEVE |  |  | NBR |  | 2
14 | PLAIN WASHER |  |  | NORYL |  | 1~2
15 | SPRING WASHER |  |  | STS304 |  | 1~2
16 | HEX BOLT |  |  | NBR |  | 1~2
17 | SHELL |  |  | STS304 |  | 1
18 | HEAD |  |  | NORYL |  | 1
19 | SLIDING BEARING |  |  | STS410 |  | 1
20 | STRAINER |  |  | STS304 |  | 1
21 | CABLE GUARD |  |  | STS304 |  | 1
22 | SCREW |  |  | STS304 |  | 8
SECTIONAL DRAWING
of PLS-6INCH M TYPE

## Test Report(PLS-7533M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 113 | 200 | 280 | 400 | 500
Dis. Head | (m) | 100 | 98 | 91.2 | 80.1 | 46 | 6.9
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0071624 | 0.022437 | 0.043976 | 0.089747 | 0.14023
Total Head | (m) | 102.4 | 100.4072 | 93.6224 | 82.544 | 48.4897 | 9.4402
Water Power | (㎾) | 0 | 1.8494 | 3.0521 | 3.7673 | 3.1615 | 0.76938
Shaft Power | (㎾) | 2.6364 | 4.2026 | 5.1785 | 5.8317 | 6.0678 | 5.8238
Pump Eff. | (%) | 0 | 44.0063 | 58.9382 | 64.6008 | 52.1037 | 13.2109
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 9 | 11.6 | 12.73 | 13.88 | 14.29 | 13.87
Motor Input | (㎾) | 3.35 | 5.34 | 6.58 | 7.41 | 7.71 | 7.4
Motor Eff. | (%) | 78.7 | 78.7 | 78.7 | 78.7 | 78.7 | 78.7
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 280 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 70 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 2.4
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 14.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78.7 | Maker | FRANKLIN | Turbin | 11 | 14
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-7533M |  | Customer |  |  |  | 2 |  | 02/2/28
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-10033M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 100 | 200 | 280 | 370 | 400 | 460 | 516
Dis. Head | (m) | 134 | 131 | 122.5 | 108 | 77 | 63 | 33 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.012871 | 0.051483 | 0.10091 | 0.1762 | 0.20593 | 0.27235 | 0.34269
Total Head | (m) | 136.4 | 133.4129 | 124.9515 | 110.5009 | 79.5762 | 65.6059 | 35.6723 | 2.7427
Water Power | (㎾) | 0 | 2.1746 | 4.0734 | 5.0433 | 4.7992 | 4.2775 | 2.6747 | 0.23068
Shaft Power | (㎾) | 3.2292 | 5.0778 | 6.6222 | 7.5348 | 7.8468 | 7.8468 | 7.7376 | 7.5036
Pump Eff. | (%) | 0 | 42.8262 | 61.5116 | 66.9329 | 61.1618 | 54.5128 | 34.5677 | 3.0743
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 10.89 | 13.53 | 16.15 | 17.8 | 18.37 | 18.37 | 18.13 | 17.7
Motor Input | (㎾) | 4.14 | 6.51 | 8.49 | 9.66 | 10.06 | 10.06 | 9.92 | 9.62
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 100 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 2.4
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | FRANKLIN | Turbin | 30 | 26
Item No. |  |  | Serial No. |  | Inspector | P.T.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-10033M |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-15033M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 100 | 140 | 280 | 390 | 450 | 520
Dis. Head | (m) | 205 | 200 | 196 | 166 | 105 | 62 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.012871 | 0.025227 | 0.10091 | 0.19576 | 0.26063 | 0.34803
Total Head | (m) | 207.3 | 202.3129 | 198.3252 | 168.4009 | 107.4958 | 64.5606 | 2.648
Water Power | (㎾) | 0 | 3.2977 | 4.5258 | 7.6858 | 6.8335 | 4.7355 | 0.22445
Shaft Power | (㎾) | 4.7077 | 7.5709 | 8.6295 | 11.4285 | 11.9658 | 11.8375 | 11.4044
Pump Eff. | (%) | 0 | 43.5577 | 52.4453 | 67.2513 | 57.1085 | 40.0043 | 1.9681
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 15.61 | 19.53 | 21.22 | 26.11 | 27.1 | 26.85 | 26.08
Motor Input | (㎾) | 5.87 | 9.44 | 10.76 | 14.25 | 14.92 | 14.76 | 14.22
Motor Eff. | (%) | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 150 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 2.3
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 28.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80.2 | Maker | FRANKLIN | Turbin | 23 | 24
Item No. |  |  | Serial No. |  | Inspector | P.T.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-15033M |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-20033M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 100 | 140 | 280 | 390 | 450 | 520
Dis. Head | (m) | 273 | 265 | 260 | 222 | 140 | 85 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.012871 | 0.025227 | 0.10091 | 0.19576 | 0.26063 | 0.34803
Total Head | (m) | 275.3 | 267.3129 | 262.3252 | 224.4009 | 142.4958 | 87.5606 | 2.648
Water Power | (㎾) | 0 | 4.3572 | 5.9863 | 10.2417 | 9.0585 | 6.4226 | 0.22445
Shaft Power | (㎾) | 7.1074 | 10.2734 | 11.5709 | 15.2184 | 15.9691 | 15.7162 | 15.1368
Pump Eff. | (%) | 0 | 42.4123 | 51.7356 | 67.2979 | 56.7248 | 40.866 | 1.4828
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 20.93 | 25.55 | 27.66 | 33.9 | 35.25 | 34.85 | 33.77
Motor Input | (㎾) | 8.71 | 12.59 | 14.18 | 18.65 | 19.57 | 19.26 | 18.55
Motor Eff. | (%) | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 15 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 200 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 2.3
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 36.7 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 81.6 | Maker | FRANKLIN | Turbin | 23 | 24
Item No. |  |  | Serial No. |  | Inspector | P.T.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-20033M |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-25033M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 239 | 314 | 367 | 412 | 453 | 489 | 523
Dis. Head | (m) | 340 | 300 | 250 | 200 | 150 | 100 | 50 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.073519 | 0.1269 | 0.17336 | 0.21847 | 0.26412 | 0.30777 | 0.35205
Total Head | (m) | 342.4 | 302.4735 | 252.5269 | 202.5734 | 152.6185 | 102.6641 | 52.7078 | 2.7521
Water Power | (㎾) | 0 | 11.7835 | 12.9248 | 12.1181 | 10.2492 | 7.5806 | 4.2012 | 0.23461
Shaft Power | (㎾) | 7.6342 | 18.1794 | 19.9096 | 20.254 | 20.2458 | 19.9916 | 19.6718 | 19.2372
Pump Eff. | (%) | 0 | 64.8177 | 64.9176 | 59.8309 | 50.6241 | 37.919 | 21.3563 | 1.2196
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 24.33 | 40.35 | 43.43 | 44.03 | 44 | 43.58 | 42.94 | 42.2
Motor Input | (㎾) | 9.31 | 22.17 | 24.28 | 24.7 | 24.69 | 24.38 | 23.99 | 23.46
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 18.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 250 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 2.4
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 45.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | FRANKLIN | Turbin | 17 | 20
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PLS-25033M |  | Customer |  |  |  | 1
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PLS-30033M)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 111 | 160 | 240 | 320 | 400 | 470
Dis. Head | (m) | 406 | 397 | 385 | 359 | 285 | 190 | 80
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.015858 | 0.032949 | 0.074136 | 0.1318 | 0.20593 | 0.28432
Total Head | (m) | 408.4 | 399.4159 | 387.4329 | 361.4741 | 287.5318 | 192.6059 | 82.6843
Water Power | (㎾) | 0 | 7.2266 | 10.1043 | 14.1409 | 14.9977 | 12.5579 | 6.3344
Shaft Power | (㎾) | 9.9285 | 16.3961 | 18.6263 | 21.6908 | 23.8218 | 24.1109 | 23.4832
Pump Eff. | (%) | 0 | 44.0753 | 54.2472 | 65.1931 | 62.9576 | 52.0839 | 26.9744
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 29.36 | 38.62 | 42.31 | 47.56 | 51.37 | 51.85 | 50.7
Motor Input | (㎾) | 12.02 | 19.85 | 22.55 | 26.26 | 28.84 | 29.19 | 28.43
Motor Eff. | (%) | 82.6 | 82.6 | 82.6 | 82.6 | 82.6 | 82.6 | 82.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 320 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 270 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 2.4
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 55.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82.6 | Maker | FRANKLIN | Turbin | 22 | 18
Item No. |  |  | Serial No. |  | Inspector | C.D.O | Run (Hr) | B/R (℃) | Test Date
Model | PLS-30033M |  | Customer |  |  |  | 3
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification