## Datasheet(PS3-0512H)
Submersible Motor Pump Data Sheet
1 | Model | PS3-0512H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 30 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 30 | m | Shaft | STS430F
10 | Rated Capacity | 35 | ℓ/min | Shell | STS304
11 | Shut off Head | 50 | m | Impeller / Diffuser | Noryl / Polyacetal
12 | Speed | 3450 | rpm | Bush bracket | Noryl
13 | Rated Efficiency | 43 | % | Head | Brass
14 | Min. Flow | 20 | ℓ/min | Base | Brass
15 | Max. Flow | 45 | ℓ/min | Coupling | STS316L
16 | Discharge Dia. | 25 | mm | Cable Guard | STS430 2B
17 | Out Dia. | 74mm(Cable Guard included)
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO (ITALY) |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.37 | kw | Stud | STS304
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Plastic
23 | Pole | 2 | p | Seal | Grafite / Allumina
24 | Max. Load Current | 4.3 | A | Diaphragm | NBR
25 | Insulation Class | F | class | Diaphragm Cover | STS304
26 | Operating Cond. | Continuous |  | Flange Cover | NBR
27 | Starting Method | Direct On Line |  | Lead Potting | NBR
28 | Out Dia. | 72 | mm | Cable Plate | STS304
29 | Max. downthrust | 120 kgf / 260 lbs |  | Bearing | STEEL
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Mechanical Seal (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 11 | stages | Lubrication | Oil Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 480 | mm | Pump | 3 | kg
37 | Motor | 372 | mm | Motor | 6.5 | kg
38 | Total | 852 | mm | Total | 9.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PS3-1012H)
Submersible Motor Pump Data Sheet
1 | Model | PS3-1012H | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 30 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 30 | m | Shaft | STS430F
10 | Rated Capacity | 60 | ℓ/min | Shell | STS304
11 | Shut off Head | 100 | m | Impeller / Diffuser | Noryl / Polyacetal
12 | Speed | 3450 | rpm | Bush bracket | Noryl
13 | Rated Efficiency | 54 | % | Head | Brass
14 | Min. Flow | 20 | ℓ/min | Base | Brass
15 | Max. Flow | 45 | ℓ/min | Coupling | STS316L
16 | Discharge Dia. | 25 | mm | Cable Guard | STS430 2B
17 | Out Dia. | 74mm(Cable Guard included)
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO (ITALY) |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | STS304
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Plastic
23 | Pole | 2 | p | Seal | Grafite / Allumina
24 | Max. Load Current | 6.2 | A | Diaphragm | NBR
25 | Insulation Class | F | class | Diaphragm Cover | STS304
26 | Operating Cond. | Continuous |  | Flange Cover | NBR
27 | Starting Method | Direct On Line |  | Lead Potting | NBR
28 | Out Dia. | 72 | mm | Cable Plate | STS304
29 | Max. downthrust | 120 kgf / 260 lbs |  | Bearing | STEEL
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Mechanical Seal (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 25 | stages | Lubrication | Oil Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 830 | mm | Pump | 5 | kg
37 | Motor | 410 | mm | Motor | 7.5 | kg
38 | Total | 1240 | mm | Total | 12.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE |  | VOLTS | HZ
PS3-0512H | 11 |  |  | 0.5 |  | 1 |  | 220 | 60
PS3-1012H | 25 |  |  | 1 |  | 1 |  | 220 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PS3-0512H | 480 |  |  | 372 |  |  | 852
PS3-1012H | 830 |  |  | 410 |  |  | 1240
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PS3-0512H | 3 |  |  | 6.5 |  |  | 9.5
PS3-1012H | 5 |  |  | 7.5 |  |  | 12.5
※MOTOR MAKER : SUMOTO (ITALY)
|  | TYPE |  |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PS3- TYPE

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD,PUMP |  |  | BRASS |  | 1
2 | O-RING |  |  | NBR |  | 1
3 | CHECK VALVE |  |  | POLYACETAL |  | 1
4 | FIXING SCREW |  |  | STS304 |  | 1
5 | GROWER |  |  | STS304 |  | 1
6 | PRESSURE WASHER |  |  | STS316L |  | 1
7 | RUBBER BUSHER |  |  | Polyurehgane PUR |  | 1
8 | VALVE SEAT |  |  | NORYL |  | 1
9 | BUSH BRACKET |  |  | NORYL |  | 1
10 | SPACER BUSH |  |  | NORYL |  | 2
11 | BUSHING |  |  | STS316L |  | 1
12 | DIFFUSE DISC |  |  | POLYACETAL |  | Stages+1
13 | DIFFUSER |  |  | POLYACETAL |  | Stages
14 | WASHER |  |  | STS304 |  | 1
15 | IMPELLER |  |  | NORYL |  | Stages
16 | SHELL |  |  | STS304 |  | 1
17 | SCREW |  |  | STS304 |  | 6
18 | STRAINER |  |  | STS430 2B |  | 1
19 | SHAFT |  |  | STS430F |  | 1
20 | COUPLING |  |  | STS316L |  | 1
21 | WASHER |  |  | STS316L |  | 1
22 | SCREW |  |  | STS304 |  | 1
23 | BASE |  |  | BRASS |  | 1
24 | CABLE GUARD |  |  | STS430 2B |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
|  | MODEL |  | PS3-0512/1012H
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PS3- TYPE

## Test Reprt(PS3-0512H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 10 | 20 | 30 | 35 | 50 | 61
Dis. Head | (m) | 50 | 45.7 | 42 | 37 | 34 | 18 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0058816 | 0.023527 | 0.052935 | 0.07205 | 0.14704 | 0.21886
Total Head | (m) | 50.8 | 46.5059 | 42.8235 | 37.8529 | 34.8721 | 18.947 | 1.0189
Water Power | (㎾) | 0 | 0.075805 | 0.1396 | 0.1851 | 0.19895 | 0.15442 | 0.01013
Shaft Power | (㎾) | 0.3774 | 0.3927 | 0.4182 | 0.4386 | 0.4386 | 0.4386 | 0.4335
Pump Eff. | (%) | 0 | 19.3034 | 33.3823 | 42.2027 | 45.3591 | 35.2071 | 2.3369
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 3.52 | 3.67 | 3.85 | 4.01 | 4.05 | 4.01 | 3.95
Motor Input | (㎾) | 0.74 | 0.77 | 0.82 | 0.86 | 0.86 | 0.86 | 0.85
Motor Eff. | (%) | 51 | 51 | 51 | 51 | 51 | 51 | 51
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.37 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 30 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 25 | 0.8
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 4.3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 51 | Maker | SUMOTO | Turbin | 26 | 25
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PS3-0512H |  | Customer |  |  |  | 2 |  | 2004.04.21
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PS3-1012H)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 10 | 20 | 30 | 40 | 50 | 61
Dis. Head | (m) | 107.5 | 99.8 | 90 | 77.2 | 59 | 35 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0058816 | 0.023527 | 0.052935 | 0.094106 | 0.14704 | 0.21886
Total Head | (m) | 108.3 | 100.6059 | 90.8235 | 78.0529 | 59.8941 | 35.947 | 1.0189
Water Power | (㎾) | 0 | 0.16399 | 0.29608 | 0.38168 | 0.39051 | 0.29297 | 0.01013
Shaft Power | (㎾) | 0.5472 | 0.6042 | 0.6726 | 0.7239 | 0.7353 | 0.7125 | 0.7011
Pump Eff. | (%) | 0 | 27.1413 | 44.0209 | 52.7254 | 53.1089 | 41.1184 | 1.4449
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 4.5 | 4.92 | 5.42 | 5.8 | 5.9 | 5.75 | 5.67
Motor Input | (㎾) | 0.96 | 1.06 | 1.18 | 1.27 | 1.29 | 1.25 | 1.23
Motor Eff. | (%) | 57 | 57 | 57 | 57 | 57 | 57 | 57
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  | 10: MOTOR SPECIFICATION; 50: TEST CONDITION
Capacity | 30 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 60 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 25 | 0.8
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 6.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57 | M/T Maker | SUMOTO | Turbin | 26 | 25
Item No. |  |  | Serial No. | X1 | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PS3-1012H | 10: Customer; 50: 2 | 2004.04.21
Checked By |  | 30: Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification