## Datasheet(PSB-1012GP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-1012GP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 90 | m | Shaft | STS410
10 | Rated Capacity | 35 | ℓ/min | Shell | STS304
11 | Shut off Head | 130 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 15 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 45 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 12 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 14 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 520 | mm | Pump | 4.5 | kg
37 | Motor | 295 | mm | Motor | 10.6 | kg
38 | Total | 815 | mm | Total | 15.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB-2012GP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-2012GP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 150 | m | Shaft | STS410
10 | Rated Capacity | 35 | ℓ/min | Shell | STS304
11 | Shut off Head | 220 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 15 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 45 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 15 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 24 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 774 | mm | Pump | 6 | kg
37 | Motor | 375 | mm | Motor | 14 | kg
38 | Total | 1149 | mm | Total | 20 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB-2032GP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-2032GP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 150 | m | Shaft | STS410
10 | Rated Capacity | 35 | ℓ/min | Shell | STS304
11 | Shut off Head | 220 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 15 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 45 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 9 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 24 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 774 | mm | Pump | 6 | kg
37 | Motor | 340 | mm | Motor | 11.4 | kg
38 | Total | 1114 | mm | Total | 17.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PSB-2033GP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-2033GP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 150 | m | Shaft | STS410
10 | Rated Capacity | 35 | ℓ/min | Shell | STS304
11 | Shut off Head | 220 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Impeller Gasket | NBR
13 | Rated Efficiency | 55 | % | Middle Casing | Noryl
14 | Min. Flow | 15 | ℓ/min | Head | Acetal(Brass inserted)
15 | Max. Flow | 45 | ℓ/min | Base | Xyron
16 | Discharge Dia. | 32 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | PVC
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 5.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 24 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 774 | mm | Pump | 6 | kg
37 | Motor | 340 | mm | Motor | 11.4 | kg
38 | Total | 1114 | mm | Total | 17.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE |  | VOLTS | HZ
PSB-1012GP | 14 |  |  | 1 |  | 1 |  | 220 | 60
PSB-1012HP | 8 |  |  | 1 |  | 1 |  | 220 | 60
PSB-1033GP | 14 |  |  | 1 |  | 3 |  | 380 | 60
PSB-1033HP | 8 |  |  | 1 |  | 3 |  | 380 | 60
PSB-2012GP | 24 |  |  | 2 |  | 1 |  | 220 | 60
PSB-2012HP | 13 | 28 |  | 2 |  | 1 |  | 220 | 60
PSB-2032GP | 24 | 28 |  | 2 |  | 3 |  | 220 | 60
PSB-2032HP | 13 | 37 |  | 2 |  | 3 |  | 220 | 60
PSB-2033GP | 24 | 37 |  | 2 |  | 3 |  | 380 | 60
PSB-2033HP | 13 |  |  | 2 |  | 3 |  | 380 | 60
PSB-3012HP | 17 | 28 |  | 3 |  | 1 |  | 220 | 60
PSB-3032HP | 17 | 28 |  | 3 |  | 3 |  | 220 | 60
PSB-3033HP | 17 | 37 |  | 3 |  | 3 |  | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PSB-1012GP | 520 |  |  | 295 |  |  | 815
PSB-1012HP | 416 |  |  | 295 |  |  | 711
PSB-1033GP | 520 |  |  | 265 |  |  | 785
PSB-1033HP | 416 |  |  | 265 |  |  | 681
PSB-2012GP | 774 |  |  | 375 |  |  | 1149
PSB-2012HP | 555 | 28 |  | 375 |  |  | 930
PSB-2032GP | 774 | 28 |  | 340 |  |  | 1114
PSB-2032HP | 555 | 37 |  | 340 |  |  | 895
PSB-2033GP | 774 | 37 |  | 340 |  |  | 1114
PSB-2033HP | 555 |  |  | 340 |  |  | 895
PSB-3012HP | 685 | 28 |  | 430 |  |  | 1115
PSB-3032HP | 685 | 28 |  | 375 |  |  | 1060
PSB-3033HP | 685 | 37 |  | 375 |  |  | 1060
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PSB-1012GP | 4.5 |  |  | 10.6 |  |  | 15.1
PSB-1012HP | 3 |  |  | 10.6 |  |  | 13.6
PSB-1033GP | 4.5 |  |  | 8.3 |  |  | 12.8
PSB-1033HP | 3 |  |  | 8.3 |  |  | 11.3
PSB-2012GP | 6 |  |  | 14 |  |  | 20
PSB-2012HP | 4.3 | 28 |  | 14 |  |  | 18.3
PSB-2032GP | 6 | 28 |  | 11.4 |  |  | 17.4
PSB-2032HP | 4.3 | 37 |  | 11.4 |  |  | 15.7
PSB-2033GP | 6 | 37 |  | 11.4 |  |  | 17.4
PSB-2033HP | 4.3 |  |  | 11.4 |  |  | 15.7
PSB-3012HP | 5.5 | 28 |  | 16.4 |  |  | 21.9
PSB-3032HP | 5.5 | 28 |  | 14.2 |  |  | 19.7
PSB-3033HP | 5.5 | 37 |  | 14.2 |  |  | 19.7
※MOTOR MAKER : SUMOTO s.r.l.
|  | TYPE |  |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PSB-GP,HP TYPE
104mm
P.L
M.L
T.L
Cable Guard
Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD,PUMP |  |  | POM + BRASS |  | 1
2 | STOP RING |  |  | STS304 |  | 1
3 | CHECK VALVE |  |  | NORYL + NBR |  | 1
4 | FIXING NUT |  |  | STS304 + NYLON |  | 1
5 | PLAIN WASHER |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | SLIDING BEARING |  |  | NBR |  | 1
8 | DIFFUSER |  |  | NORYL |  | Stages
9 | SLIDING BEARING |  |  | NBR |  | Stages
10 | UPTHRUST WASHER |  |  | STS304 |  | Stages
11 | MIDDLE CASING |  |  | NORYL |  | Stages
12 | IMPELLER |  |  | NORYL+STS304 |  | Stages
13 | IMPELLER GASKET |  |  | NBR |  | Stages
14 | MIDDLE SPACER |  |  | NORYL |  | 1~2
15 | SLEEVE |  |  | STS304 |  | 1~2
16 | SLIDING BEARING |  |  | NBR |  | 1~2
17 | SHELL |  |  | STS304 |  | 1
18 | LOWER SPACER |  |  | NORYL |  | 1
19 | SHAFT |  |  | STS410 |  | 1
20 | COUPLING |  |  | STS304 |  | 1
21 | SCREW |  |  | STS304 |  | 1
22 | STOPPER |  |  | STS304 |  | 1
23 | BASE |  |  | NORYL |  | 1
24 | SCREW |  |  | STS304 |  | 1
25 | CABLE GUARD |  |  | HD PE |  | 1
26 | STRAINER |  |  | STS304 |  | 1
27 | SCREW |  |  | STS304 |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PSB-GP,HP TYPE
22
27
26
23
24
25
13
20
21
18
16
15
14
12
3
19
17
7
11
10
8
9
5
6
4
1
2

## Test Report(PSB-1012GP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 15 | 25 | 35 | 45 | 55 | 66
Dis. Head | (m) | 132 | 122 | 110 | 94 | 71 | 45 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0049299 | 0.013694 | 0.026841 | 0.044369 | 0.06628 | 0.095444
Total Head | (m) | 133.55 | 123.5549 | 111.5637 | 95.5768 | 72.5944 | 46.6163 | 1.6454
Water Power | (㎾) | 0 | 0.30209 | 0.45462 | 0.54527 | 0.53248 | 0.41791 | 0.017702
Shaft Power | (㎾) | 0.62776 | 0.88854 | 0.9617 | 0.9912 | 0.99002 | 0.95639 | 0.92512
Pump Eff. | (%) | 0 | 33.9987 | 47.2728 | 55.0107 | 53.7847 | 43.6971 | 1.9134
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.37 | 8.87 | 9.34 | 9.54 | 9.52 | 9.29 | 9.1
Motor Input | (㎾) | 1.064 | 1.506 | 1.63 | 1.68 | 1.678 | 1.621 | 1.568
Motor Eff. | (%) | 59 | 59 | 59 | 59 | 59 | 59 | 59
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 90 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1.55
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 12 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 59 | Maker | Sumoto | Turbin | 26 | 26
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSB-1012GP |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB-2012GP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20 | 33.6 | 35 | 45 | 60 | 60.5 | 70.4
Dis. Head | (m) | 219 | 209 | 179 | 173 | 138 | 61 | 59 | 0.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0087643 | 0.024736 | 0.026841 | 0.044369 | 0.078879 | 0.080199 | 0.10859
Total Head | (m) | 220 | 210.0088 | 180.0247 | 174.0268 | 139.0444 | 62.0789 | 60.0802 | 1.2086
Water Power | (㎾) | 0 | 0.68463 | 0.98596 | 0.99282 | 1.0199 | 0.60713 | 0.59248 | 0.013869
Shaft Power | (㎾) | 1.3532 | 1.8108 | 1.9972 | 2.0094 | 2.0182 | 1.8625 | 1.855 | 1.749
Pump Eff. | (%) | 0 | 37.8072 | 49.3681 | 49.4089 | 50.5337 | 32.5973 | 31.939 | 0.79298
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 10.49 | 13.37 | 14.61 | 14.73 | 14.78 | 13.72 | 13.7 | 12.97
Motor Input | (㎾) | 1.99 | 2.663 | 2.937 | 2.955 | 2.968 | 2.739 | 2.728 | 2.572
Motor Eff. | (%) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 150 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 15 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68 | Maker | Sumoto | Turbin | 21 | 24
Item No. | X2 |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-2012GP |  | Customer |  |  |  | 0.5 |  | 2013.11.11
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB-2032GP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20 | 35 | 40 | 50 | 60 | 74
Dis. Head | (m) | 222 | 194 | 163 | 146 | 110 | 65 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0087643 | 0.026841 | 0.035057 | 0.054777 | 0.078879 | 0.11998
Total Head | (m) | 223.65 | 195.6588 | 164.6768 | 147.6851 | 111.7048 | 66.7289 | 1.77
Water Power | (㎾) | 0 | 0.63785 | 0.93948 | 0.96291 | 0.91039 | 0.65261 | 0.02135
Shaft Power | (㎾) | 1.1169 | 1.6571 | 1.752 | 1.7593 | 1.7447 | 1.6717 | 1.6352
Pump Eff. | (%) | 0 | 38.4918 | 53.6234 | 54.7324 | 52.1805 | 39.0386 | 1.3056
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 5.4 | 7 | 7.35 | 7.38 | 7.32 | 7.05 | 6.92
Motor Input | (㎾) | 1.53 | 2.27 | 2.4 | 2.41 | 2.39 | 2.29 | 2.24
Motor Eff. | (%) | 73 | 73 | 73 | 73 | 73 | 73 | 73
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 150 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1.65
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73 | Maker | Sumoto | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSB-2032GP |  | Customer
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(PSB-2033GP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20 | 29.6 | 35 | 45 | 58.5 | 69
Dis. Head | (m) | 214 | 199 | 179 | 164 | 128 | 59 | 0.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0087643 | 0.019197 | 0.026841 | 0.044369 | 0.074984 | 0.10432
Total Head | (m) | 215 | 200.0088 | 180.0192 | 165.0268 | 129.0444 | 60.075 | 1.2043
Water Power | (㎾) | 0 | 0.65203 | 0.86856 | 0.94148 | 0.94654 | 0.57285 | 0.013545
Shaft Power | (㎾) | 1.2698 | 1.7708 | 1.8892 | 1.9262 | 1.9336 | 1.8019 | 1.7005
Pump Eff. | (%) | 0 | 36.8207 | 45.9744 | 48.877 | 48.9517 | 31.7912 | 0.79652
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.64 | 4.55 | 4.78 | 4.84 | 4.86 | 4.61 | 4.41
Motor Input | (㎾) | 1.716 | 2.393 | 2.553 | 2.603 | 2.613 | 2.435 | 2.298
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 35 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 150 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 5.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | Sumoto | Turbin | 20 | 21
Item No. | X2 |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-2033GP |  | Customer |  |  |  | 0.5 |  | 2013.11.19
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification