## Datasheet(2012QP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-2012QP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 32 | m | Shaft | STS410
10 | Rated Capacity | 180 | ℓ/min | Shell | STS304
11 | Shut off Head | 50 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Liner Ring | STS304
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | POM+Brass
15 | Max. Flow | 250 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 50 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 15 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 550 | mm | Pump | 5.5 | kg
37 | Motor | 375 | mm | Motor | 14 | kg
38 | Total | 925 | mm | Total | 19.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(2033QP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-2033QP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 32 | m | Shaft | STS410
10 | Rated Capacity | 180 | ℓ/min | Shell | STS304
11 | Shut off Head | 50 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Liner Ring | STS304
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | POM+Brass
15 | Max. Flow | 250 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 50 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 5.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 550 | mm | Pump | 5.5 | kg
37 | Motor | 340 | mm | Motor | 11.4 | kg
38 | Total | 890 | mm | Total | 16.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3012QP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-3012QP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 45 | m | Shaft | STS410
10 | Rated Capacity | 180 | ℓ/min | Shell | STS304
11 | Shut off Head | 65 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Liner Ring | STS304
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | POM+BRASS
15 | Max. Flow | 250 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 50 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 16.9 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 830 | mm | Pump | 6.5 | kg
37 | Motor | 430 | mm | Motor | 16.4 | kg
38 | Total | 1260 | mm | Total | 22.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(3033QP)
Submersible Motor Pump Data Sheet
1 | Model | PSB-3033QP | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 45 | m | Shaft | STS410
10 | Rated Capacity | 180 | ℓ/min | Shell | STS304
11 | Shut off Head | 65 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Liner Ring | STS304
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | POM+BRASS
15 | Max. Flow | 250 | ℓ/min | Base | Noryl
16 | Discharge Dia. | 50 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 7.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 830 | mm | Pump | 6.5 | kg
37 | Motor | 375 | mm | Motor | 14.2 | kg
38 | Total | 1205 | mm | Total | 20.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5533Q)
Submersible Motor Pump Data Sheet
1 | Model | PSB-5533Q | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 70 | m | Shaft | STS410
10 | Rated Capacity | 180 | ℓ/min | Shell | STS304
11 | Shut off Head | 110 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Liner Ring | STS304
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | HBsC1
15 | Max. Flow | 250 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 50 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kw | Stator Ends | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 12 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 662 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 945 | mm | Pump | 9 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 1500 | mm | Total | 32.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(7533Q)
Submersible Motor Pump Data Sheet
1 | Model | PSB4-7533Q | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 110 | m | Shaft | STS410
10 | Rated Capacity | 180 | ℓ/min | Shell | STS304
11 | Shut off Head | 160 | m | Impeller / Diffuser | Noryl
12 | Speed | 3450 | rpm | Liner Ring | STS304
13 | Rated Efficiency | 60 | % | Sleeve | STS304
14 | Min. Flow | 100 | ℓ/min | Head | HBsC1
15 | Max. Flow | 250 | ℓ/min | Base | HBsC1
16 | Discharge Dia. | 50 | mm | Coupling | STS304
17 | Out Dia. | 101mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO s.r.l. |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 17.3 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 94 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 662 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 19 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1275 | mm | Pump | 11 | kg
37 | Motor | 675 | mm | Motor | 29.4 | kg
38 | Total | 1950 | mm | Total | 40.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing(PSB-QP)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE |  | VOLTS | HZ
PLS-2012QP | 6 |  |  | 2 |  | 1 |  | 220 | 60
PLS-2032QP | 6 |  |  | 2 |  | 3 |  | 220 | 60
PLS-2033QP | 6 |  |  | 2 |  | 3 |  | 380 | 60
PLS-3012QP | 8 |  |  | 3 |  | 1 |  | 220 | 60
PLS-3032QP | 8 |  |  | 3 |  | 3 |  | 220 | 60
PLS-3033QP | 8 |  |  | 3 |  | 3 |  | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PLS-2012QP | 550 |  |  | 375 |  |  | 925
PLS-2032QP | 550 |  |  | 340 |  |  | 890
PLS-2033QP | 550 |  |  | 340 |  |  | 890
PLS-3012QP | 830 |  |  | 430 |  |  | 1260
PLS-3032QP | 830 |  |  | 375 |  |  | 1205
PLS-3033QP | 830 |  |  | 375 |  |  | 1205
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PLS-2012QP | 5.5 |  |  | 14 |  |  | 19.5
PLS-2032QP | 5.5 |  |  | 11.4 |  |  | 16.9
PLS-2033QP | 5.5 |  |  | 11.4 |  |  | 16.9
PLS-3012QP | 6.5 | 28 |  | 16.4 |  |  | 22.9
PLS-3032QP | 6.5 |  |  | 14.2 |  |  | 20.7
PLS-3033QP | 6.5 |  |  | 14.2 |  |  | 20.7
※MOTOR MAKER : SUMOTO s.r.l.
※DISCHARGE CONNECTION : 2" (50mm)
|  | TYPE |  |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PSB-QP MODEL

## Outline Drawing(PSB-Q)
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | STAGES |  |  | POWER RESOURCE
|  |  |  | HP |  | PHASE | VOLTS | HZ
PSB-5532Q | 13 | 28 |  | 5 |  | 3 | 220 | 60
PSB-5533Q | 13 | 28 |  | 5 |  | 3 | 380 | 60
PSB4-7532Q | 19 |  |  | 7.5 |  | 3 | 220 | 60
PSB4-7533Q | 19 |  |  | 7.5 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | P.L |  |  | M.L |  |  | T.L
PSB-5532Q | 945 |  |  | 555 |  |  | 1500
PSB-5533Q | 945 |  |  | 555 |  |  | 1500
PSB4-7532Q | 1275 |  |  | 675 |  |  | 1950
PSB4-7533Q | 1275 |  |  | 675 |  |  | 1950
WEIGHT(kg)
MODEL | PUMP |  |  | MOTOR |  |  | TOTAL
PSB-5532Q | 9 |  |  | 23.4 |  |  | 32.4
PSB-5533Q | 9 |  |  | 23.4 |  |  | 32.4
PSB4-7532Q | 11 |  |  | 29.4 |  |  | 40.4
PSB4-7533Q | 11 |  |  | 29.4 |  |  | 40.4
※MOTOR MAKER : SUMOTO s.r.l.
※DISCHARGE DIA. : 50mm
|  | TYPE |  |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
OUTLINE DRAWING
of PSB-Q MODEL
104mm
P.L
M.L
T.L
Cable Guard
Included

## Sectional Drawing(PSB-QP)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD |  |  | POM+Brass |  | 1
2 | STOPPER |  |  | STS304 |  | 1
3 | CHECK VALVE |  |  | NORYL + NBR |  | 1
4 | FIXING NUT |  |  | STS304 + NYLON |  | 1
5 | PLAIN WASHER |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | SLIDING BEARING |  |  | NBR |  | 1
8 | SLEEVE |  |  | STS304 |  | 1
9 | DIFFUSER COVER |  |  | NORYL+STS304 |  | Stages
10 | DIFLECTOR |  |  | NORYL |  | Stages
11 | DIFFUSER BODY |  |  | NORYL |  | Stages
12 | SLIDING BEARING |  |  | NBR |  | Stages
13 | SLEEVE |  |  | STS304 |  | Stages
14 | UPTHRUST WASHER |  |  | STS304 |  | Stages
15 | IMPELLER |  |  | NORYL |  | Stages
16 | SHAFT |  |  | STS410 |  | 1
17 | SHELL |  |  | STS304 |  | 1
18 | DIFFUSER COVER |  |  | NORYL |  | 1
19 | LOWER SPACER |  |  | NORYL |  | 1
20 | COUPLING |  |  | STS304 |  | 1
21 | SCREW |  |  | STS304 |  | 1
22 | STOPPER |  |  | STS304 |  | 1
23 | STRAINER |  |  | STS304 |  | 1
24 | BASE |  |  | BRASS |  | 1
25 | SCREW |  |  | STS304 |  | 1
26 | CABLE GUARD |  |  | PVC |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PSB-QP Model

## Sectional Drawing(PSB-Q)
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | HEAD,PUMP |  |  | BRASS |  | 1
2 | STOP RING |  |  | STS304 |  | 1
3 | CHECK VALVE |  |  | NORYL + NBR |  | 1
4 | FIXING NUT |  |  | STS304 + NYLON |  | 1
5 | PLAIN WASHER |  |  | STS304 |  | 1
6 | SLEEVE |  |  | STS304 |  | 1
7 | SLIDING BEARING |  |  | NBR |  | 1
8 | SLEEVE |  |  | STS304 |  | 1
9 | DIFFUSER |  |  | NORYL |  | Stages
10 | SLIDING BEARING |  |  | NBR |  | Stages
11 | UPTHRUST WASHER |  |  | STS304 |  | Stages
12 | MIDDLE CASING |  |  | NORYL |  | Stages
13 | IMPELLER |  |  | NORYL+STS304 |  | Stages
14 | IMPELLER GASKET |  |  | NBR |  | Stages
15 | MIDDLE SPACER |  |  | NORYL |  | 1~2
16 | SLEEVE |  |  | STS304 |  | 1~2
17 | SLIDING BEARING |  |  | NBR |  | 1~2
18 | SHELL |  |  | STS304 |  | 1
19 | LOWER SPACER |  |  | NORYL |  | 1
20 | SHAFT |  |  | STS410 |  | 1
21 | COUPLING |  |  | STS304 |  | 1
22 | SCREW |  |  | STS304 |  | 1
23 | STOP RING |  |  | STS304 |  | 1
24 | BASE |  |  | BRASS |  | 1
25 | STRAINER |  |  | STS304 |  | 1
26 | SCREW |  |  | STS304 |  | 6
27 | CABLE GUARD |  |  | STS304 |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
SECTIONAL DRAWING
of PSB-Q MODEL
13
25
24
26
21
23
22
12
19
14
20
18
27
7
11
16
17
15
9
10
8
6
5
4
3
2
1

## Test Report(2012QP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 120 | 180 | 240 | 325
Dis. Head | (m) | 51.3 | 49.5 | 42.5 | 36 | 25.5 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.052935 | 0.1191 | 0.21174 | 0.38828
Total Head | (m) | 52 | 50.2092 | 43.2529 | 36.8191 | 26.4117 | 5.0883
Water Power | (㎾) | 0 | 0.4092 | 0.84603 | 1.0803 | 1.0332 | 0.26955
Shaft Power | (㎾) | 1.0948 | 1.2988 | 1.5708 | 1.8428 | 1.8904 | 1.836
Pump Eff. | (%) | 0 | 31.5064 | 53.8597 | 58.6213 | 54.6565 | 14.6815
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.4 | 8.5 | 10.1 | 12.9 | 13.11 | 12.9
Motor Input | (㎾) | 1.61 | 1.91 | 2.31 | 2.71 | 2.78 | 2.7
Motor Eff. | (%) | 68 | 68 | 68 | 68 | 68 | 68
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 180 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 32 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.7
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 15 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68 | Maker | SUMOTO | Turbin | 13 | 17
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSB-2012QP |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(2033QP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 60 | 120 | 180 | 240 | 323
Dis. Head | (m) | 50.3 | 47.5 | 42 | 36 | 26 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013234 | 0.052935 | 0.1191 | 0.21174 | 0.38352
Total Head | (m) | 51 | 48.2132 | 42.7529 | 36.8191 | 26.9117 | 5.0835
Water Power | (㎾) | 0 | 0.47153 | 0.83625 | 1.0803 | 1.0528 | 0.26764
Shaft Power | (㎾) | 1.2045 | 1.5111 | 1.6863 | 1.8615 | 1.8907 | 1.8469
Pump Eff. | (%) | 0 | 31.2041 | 49.5907 | 58.0324 | 55.6824 | 14.4914
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.61 | 4.02 | 4.41 | 4.72 | 4.77 | 4.71
Motor Input | (㎾) | 1.65 | 2.07 | 2.31 | 2.55 | 2.59 | 2.53
Motor Eff. | (%) | 73 | 73 | 73 | 73 | 73 | 73
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 180 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 32 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.7
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 5.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73 | Maker | SUMOTO | Turbin | 20 | 17
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSB-2033QP |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3012QP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 100 | 140 | 180 | 230 | 279 | 323
Dis. Head | (m) | 70 | 67.4 | 59 | 52.4 | 45.2 | 33.8 | 19 | 2.3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.03676 | 0.07205 | 0.1191 | 0.19446 | 0.28615 | 0.38352
Total Head | (m) | 71 | 68.4092 | 60.0368 | 53.4721 | 46.3191 | 34.9945 | 20.2861 | 3.6835
Water Power | (㎾) | 0 | 0.55753 | 0.9786 | 1.2202 | 1.359 | 1.3119 | 0.92255 | 0.19393
Shaft Power | (㎾) | 1.6706 | 2.0164 | 2.2088 | 2.3586 | 2.49 | 2.5141 | 2.4452 | 2.3529
Pump Eff. | (%) | 0 | 27.65 | 44.3044 | 51.735 | 54.5791 | 52.1832 | 37.7285 | 8.2422
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 10.87 | 13.06 | 14.35 | 15.29 | 16.2 | 16.38 | 15.91 | 15.25
Motor Input | (㎾) | 2.353 | 2.84 | 3.111 | 3.322 | 3.507 | 3.541 | 3.444 | 3.314
Motor Eff. | (%) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 180 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 45 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 16.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 71 | Maker | Sumoto | Turbin | 21 | 24
Item No. | X2 |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-3012QP |  | Customer |  |  |  | 0.5 |  | 2013.11.12
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(3033QP)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 99 | 140 | 180 | 230 | 277 | 322
Dis. Head | (m) | 69 | 66.9 | 59 | 52.2 | 45.5 | 33.1 | 19 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.036029 | 0.07205 | 0.1191 | 0.19446 | 0.28206 | 0.38115
Total Head | (m) | 70 | 67.9092 | 60.036 | 53.2721 | 46.6191 | 34.2945 | 20.2821 | 3.3811
Water Power | (㎾) | 0 | 0.55346 | 0.9688 | 1.2157 | 1.3678 | 1.2857 | 0.91576 | 0.17746
Shaft Power | (㎾) | 1.6178 | 1.9897 | 2.1818 | 2.3348 | 2.466 | 2.4983 | 2.433 | 2.3505
Pump Eff. | (%) | 0 | 27.8155 | 44.4048 | 52.0685 | 55.4665 | 51.464 | 37.6389 | 7.55
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.8 | 5.44 | 5.79 | 6.04 | 6.27 | 6.32 | 6.2 | 6.05
Motor Input | (㎾) | 2.157 | 2.653 | 2.909 | 3.113 | 3.288 | 3.331 | 3.244 | 3.134
Motor Eff. | (%) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 180 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 45 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 7.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 75 | Maker | Sumoto | Turbin | 17 | 21
Item No. | X2 |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-3033QP |  | Customer |  |  |  | 0.5 |  | 2013.11.21
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5533Q)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 60 | 136 | 185 | 230 | 260 | 300 | 338
Dis. Head | (m) | 115 | 110 | 89 | 75 | 57 | 44 | 24 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013234 | 0.067992 | 0.12581 | 0.19446 | 0.2485 | 0.33084 | 0.41996
Total Head | (m) | 116 | 111.0132 | 90.068 | 76.1258 | 58.1945 | 45.2485 | 25.3308 | 2.42
Water Power | (㎾) | 0 | 1.0857 | 1.9966 | 2.2956 | 2.1817 | 1.9176 | 1.2387 | 0.13333
Shaft Power | (㎾) | 2.6919 | 3.3957 | 3.8479 | 4.0896 | 4.0918 | 4.0029 | 3.8456 | 3.6678
Pump Eff. | (%) | 0 | 31.9733 | 51.889 | 56.1325 | 53.3186 | 47.9058 | 32.2103 | 3.6351
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.6 | 8.77 | 9.61 | 10.45 | 10.05 | 9.88 | 9.58 | 9.25
Motor Input | (㎾) | 3.542 | 4.468 | 5.063 | 5.381 | 5.384 | 5.267 | 5.06 | 4.826
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 180 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 4 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 70 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 12 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | Sumoto | Turbin | 17 | 21
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSB-5533Q |  | Customer |  |  |  | 0.5 |  | 2013.11.21
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(7533Q)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 70 | 170 | 240 | 300 | 327
Dis. Head | (m) | 163 | 155 | 119.3 | 80 | 35 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.018013 | 0.10624 | 0.21174 | 0.33084 | 0.39307
Total Head | (m) | 163.8 | 155.818 | 120.2062 | 81.0117 | 36.1308 | 1.1931
Water Power | (㎾) | 0 | 1.7779 | 3.3309 | 3.1692 | 1.7668 | 0.063592
Shaft Power | (㎾) | 3.2956 | 4.6123 | 5.5902 | 5.6133 | 5.3438 | 5.2437
Pump Eff. | (%) | 0 | 38.5466 | 59.5849 | 56.4584 | 33.0626 | 1.2127
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 10.73 | 12.6 | 14.14 | 14.1 | 13.7 | 13.53
Motor Input | (㎾) | 4.28 | 5.99 | 7.26 | 7.29 | 6.94 | 6.81
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 180 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 110 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.8
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 17.3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77 | Maker | SUMOTO | Turbin | 30 | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSB4-7533Q |  | Customer |  |  |  | 3
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification