## Datasheet(14-3)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-14-3_MF4-2012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 23 | m | Discharge Piece | STS304
10 | Rated Capacity | 230 | ℓ/min | Impeller | STS304
11 | Shut off Head | 27 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 350 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kW | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 13.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 375 | mm | Pump | 3.7 | kg
37 | Motor | 384 | mm | Motor | 14.5 | kg
38 | Total | 759 | mm | Total | 18.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(14-3)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-14-3_MF4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 23 | m | Discharge Piece | STS304
10 | Rated Capacity | 230 | ℓ/min | Impeller | STS304
11 | Shut off Head | 27 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 350 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | Kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 4.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 375 | mm | Pump | 3.7 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 721 | mm | Total | 16.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(14-5)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-14-5_MF4-3012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 36 | m | Discharge Piece | STS304
10 | Rated Capacity | 230 | ℓ/min | Impeller | STS304
11 | Shut off Head | 45 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 350 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 17 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 505 | mm | Pump | 5 | kg
37 | Motor | 560 | mm | Motor | 20 | kg
38 | Total | 1065 | mm | Total | 25 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(14-5)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-14-5_MF4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 36 | m | Discharge Piece | STS304
10 | Rated Capacity | 230 | ℓ/min | Impeller | STS304
11 | Shut off Head | 45 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 350 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 6.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 505 | mm | Pump | 5 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 1005 | mm | Total | 22 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(14-8)
Submersible Motor Pump Data Sheet
1 | Model | PSS-14-8_MF4-5033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 55 | m | Discharge Piece | STS304
10 | Rated Capacity | 230 | ℓ/min | Impeller | STS304
11 | Shut off Head | 70 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 350 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS410
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 700 | mm | Pump | 7 | kg
37 | Motor | 600 | mm | Motor | 25 | kg
38 | Total | 1300 | mm | Total | 32 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(14-12)
Submersible Motor Pump Data Sheet
1 | Model | PSS-14-12_MF4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 85 | m | Discharge Piece | STS304
10 | Rated Capacity | 230 | ℓ/min | Impeller | STS304
11 | Shut off Head | 105 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 350 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 16 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 12 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 960 | mm | Pump | 9.5 | kg
37 | Motor | 752 | mm | Motor | 31.8 | kg
38 | Total | 1712 | mm | Total | 41.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PSS-14-3 | MF4-2012 | 3 |  |  | 2 |  | 1 | 220 | 60
| MF4-2033 | [5 empty] | 3 | 380 | 60
PSS-14-5 | MF4-3012 | 5 |  |  | 3 |  | 1 | 220 | 60
| MF4-3033 | [5 empty] | 3 | 380 | 60
PSS-14-8 | MF4-5033 | 8 |  |  | 5 |  | 3 | 380 | 60
PSS-14-12 | MF4-7533 | 12 |  |  | 7 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-14-3 | MF4-2012 | 375 |  |  | 384 |  |  | 759
| MF4-2033 |  |  |  | 346 |  |  | 346
PSS-14-5 | MF4-3012 | 505 |  |  | 560 |  |  | 1065
| MF4-3033 |  |  |  | 500 |  |  | 500
PSS-14-8 | MF4-5033 | 700 |  |  | 600 |  |  | 1300
PSS-14-12 | MF4-7533 | 960 |  |  | 752 |  |  | 1712
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-14-3 | MF4-2012 | 3.7 |  |  | 14.5 |  |  | 18.2
| MF4-2033 |  |  |  | 13.1 |  |  | 16.8
PSS-14-5 | MF4-3012 | 5 |  |  | 20 |  |  | 25
| MF4-3033 |  |  |  | 17 |  |  | 22
PSS-14-8 | MF4-5033 | 7 |  |  | 25 |  |  | 32
PSS-14-12 | MF4-7533 | 9.5 |  |  | 31.8 |  |  | 41.3
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 2"
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-14 Series
98mm
P.L
M.L
T.L
P.L
M.L
T.L
Cable Guard Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge piece |  |  | STS304 |  | 1
2 | Stop ring |  |  | - |  | 1
4 | Check Valve |  |  | STS304 |  | 1
6 | Split cone |  |  |  |  | Stages
7 | Impeller |  |  |  |  | Stages
8 | Split cone nut |  |  |  |  | Stages
9 | Neck ring |  |  | NBR |  | Stages
10 | Diffuser |  |  | STS304 |  | Stages
11 | Guide |  |  |  |  | 1
12 | Strainer |  |  |  |  | 1
13 | Suction interconnector |  |  |  |  | 1
14 | Pump shaft/coupling |  |  | STS431/304 |  | 1
15 | Strap |  |  | STS304 |  | 4
16 | Nut |  |  |  |  | 4
17 | Cable guard |  |  |  |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-14 Series

## Test Report(14-3)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 61 | 130 | 201 | 264 | 301 | 365 | 410
Dis. Head | (m) | 28 | 27.9 | 26.1 | 23.6 | 20 | 17.4 | 11 | 3.2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013679 | 0.062125 | 0.14852 | 0.2562 | 0.33305 | 0.48974 | 0.61794
Total Head | (m) | 29 | 28.9137 | 27.1621 | 24.7485 | 21.2562 | 18.7331 | 12.4897 | 4.8179
Water Power | (㎾) | 0 | 0.28749 | 0.57557 | 0.81084 | 0.9147 | 0.9191 | 0.74308 | 0.32198
Shaft Power | (㎾) | 0.74048 | 0.74902 | 1.0943 | 1.3072 | 1.439 | 1.4867 | 1.5379 | 1.4952
Pump Eff. | (%) | 0 | 38.3818 | 52.5946 | 62.0269 | 63.5669 | 61.8233 | 48.317 | 21.5344
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.89 | 2.9 | 3.34 | 3.69 | 3.9 | 3.98 | 4.07 | 3.98
Motor Input | (㎾) | 1.04 | 1.052 | 1.537 | 1.836 | 2.021 | 2.088 | 2.16 | 2.1
Motor Eff. | (%) | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2 | 71.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 230 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 23 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 71.2 | Maker | FRANKLIN | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector | S.W.H | Run (Hr) | B/R (℃) | Test Date
Model | PSS-14-3_MF4-2033 |  | Customer |  |  |  | 2 |  | 2006.04.07
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(14-5)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 80.6 | 160 | 240.7 | 297 | 320 | 352 | 415.7
Dis. Head | (m) | 46 | 45 | 42 | 37 | 30 | 26 | 20 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023881 | 0.094106 | 0.21298 | 0.32426 | 0.37643 | 0.45547 | 0.63524
Total Head | (m) | 47 | 46.0239 | 43.0941 | 38.213 | 31.3243 | 27.3764 | 21.4555 | 5.6352
Water Power | (㎾) | 0 | 0.60465 | 1.1239 | 1.4993 | 1.5164 | 1.428 | 1.231 | 0.38184
Shaft Power | (㎾) | 1.1515 | 1.4791 | 1.8704 | 2.1917 | 2.3142 | 2.3408 | 2.3492 | 2.1581
Pump Eff. | (%) | 0 | 40.8798 | 60.0884 | 68.4059 | 65.5276 | 61.0028 | 52.4021 | 17.6933
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 8.24 | 10.14 | 12.59 | 14.69 | 15.5 | 15.71 | 15.74 | 14.44
Motor Input | (㎾) | 1.645 | 2.113 | 2.672 | 3.131 | 3.306 | 3.344 | 3.356 | 3.083
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 230 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 36 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 17.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | FRANKLIN | Turbin | 40 | 26
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-14-5_MF4-3012 |  | Customer |  |  |  | 2 |  | 2006.09.12
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(14-5)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 80 | 160 | 240 | 291 | 320 | 348 | 412.6
Dis. Head | (m) | 46 | 45 | 41 | 36 | 30 | 25 | 20 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023527 | 0.094106 | 0.21174 | 0.31129 | 0.37643 | 0.44518 | 0.6258
Total Head | (m) | 47 | 46.0235 | 42.0941 | 37.2117 | 31.3113 | 26.3764 | 21.4452 | 5.6258
Water Power | (㎾) | 0 | 0.60015 | 1.0978 | 1.4557 | 1.4852 | 1.3758 | 1.2165 | 0.37836
Shaft Power | (㎾) | 1.1251 | 1.4611 | 1.8585 | 2.1601 | 2.2648 | 2.2941 | 2.3021 | 2.1279
Pump Eff. | (%) | 0 | 41.0758 | 59.0684 | 67.3905 | 65.5768 | 59.9713 | 52.8402 | 17.7806
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.97 | 4.37 | 4.97 | 5.46 | 5.66 | 5.71 | 5.73 | 5.42
Motor Input | (㎾) | 1.537 | 1.996 | 2.539 | 2.951 | 3.094 | 3.134 | 3.145 | 2.907
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 230 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 36 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin | 44 | 30
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-14-5_MF4-3033 |  | Customer |  |  |  | 2 |  | 06/09/09
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(14-8)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 80.6 | 160 | 240 | 318 | 400 | 419.6
Dis. Head | (m) | 72 | 71 | 65 | 56 | 40 | 12 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023881 | 0.094106 | 0.21174 | 0.37173 | 0.58816 | 0.64722
Total Head | (m) | 73 | 72.0239 | 66.0941 | 57.2117 | 41.3717 | 13.5882 | 5.6472
Water Power | (㎾) | 0 | 0.94624 | 1.7237 | 2.2381 | 2.1445 | 0.88595 | 0.38624
Shaft Power | (㎾) | 1.9447 | 2.4882 | 3.1436 | 3.6307 | 3.8422 | 3.6137 | 3.5126
Pump Eff. | (%) | 0 | 38.0296 | 54.8334 | 61.6441 | 55.8128 | 24.5162 | 10.9959
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 6.59 | 7.2 | 8.1 | 8.86 | 9.21 | 8.85 | 8.69
Motor Input | (㎾) | 2.519 | 3.223 | 4.072 | 4.703 | 4.977 | 4.681 | 4.55
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 232 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 42 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin | 63 | 39
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-14-8_MF4-5033 |  | Customer |  |  |  | 2 |  | 06/09/13
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(14-12)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 80.6 | 160 | 240 | 320.9 | 415.2
Dis. Head | (m) | 108 | 107 | 99 | 85 | 60 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023881 | 0.094106 | 0.21174 | 0.37855 | 0.63371
Total Head | (m) | 109 | 108.0239 | 100.0941 | 86.2117 | 61.3785 | 5.6337
Water Power | (㎾) | 0 | 1.4192 | 2.6105 | 3.3726 | 3.2105 | 0.38128
Shaft Power | (㎾) | 2.7417 | 3.5609 | 4.4948 | 5.126 | 5.4057 | 4.7486
Pump Eff. | (%) | 0 | 39.8552 | 58.0777 | 65.7943 | 59.3912 | 8.0293
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 8.85 | 9.99 | 11.47 | 12.63 | 13.15 | 11.95
Motor Input | (㎾) | 3.705 | 4.812 | 6.074 | 6.927 | 7.305 | 6.417
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 230 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 85 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 16 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin | 58 | 43
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-14-12_MF4-7533 |  | Customer |  |  |  | 2 |  | 06/09/15
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification