## DataSheet(PSS-160-1-A)
Submersible Motor Pump Data Sheet
1 | Model | PSS-160-1-A_MS6-20033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 15 | m | Discharge Piece | STS304
10 | Rated Capacity | 3000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 35 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 1800 | ℓ/min | Coupling | STS304
15 | Max. Flow | 3800 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 150 | mm | Strainer | STS304
17 | Out Dia. | 215mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 15 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 38 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 652 | mm | Pump | 31 | kg
37 | Motor | 760 | mm | Motor | 54 | kg
38 | Total | 1412 | mm | Total | 85 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(PSS-160-1)
Submersible Motor Pump Data Sheet
1 | Model | PSS-160-1_MS6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 25 | m | Discharge Piece | STS304
10 | Rated Capacity | 3000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 48 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 1800 | ℓ/min | Coupling | STS304
15 | Max. Flow | 3800 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 150 | mm | Strainer | STS304
17 | Out Dia. | 215mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 54.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 1020 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 652 | mm | Pump | 31 | kg
37 | Motor | 890 | mm | Motor | 70 | kg
38 | Total | 1542 | mm | Total | 101 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(PSS-160-2-AA)
Submersible Motor Pump Data Sheet
1 | Model | PSS-160-2-AA_MS6-40033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 38 | m | Discharge Piece | STS304
10 | Rated Capacity | 3000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 65 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 1800 | ℓ/min | Coupling | STS304
15 | Max. Flow | 3800 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 150 | mm | Strainer | STS304
17 | Out Dia. | 215mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 30 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 75 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 2040 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 807 | mm | Pump | 37 | kg
37 | Motor | 1030 | mm | Motor | 90 | kg
38 | Total | 1837 | mm | Total | 127 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(PSS-160-2-A)
Submersible Motor Pump Data Sheet
1 | Model | PSS-160-2-A_MS6-50033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 50 | m | Discharge Piece | STS304
10 | Rated Capacity | 3000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 78 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 1800 | ℓ/min | Coupling | STS304
15 | Max. Flow | 3800 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 150 | mm | Strainer | STS304
17 | Out Dia. | 215mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 37 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 96 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 2040 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 807 | mm | Pump | 37 | kg
37 | Motor | 1170 | mm | Motor | 101 | kg
38 | Total | 1977 | mm | Total | 138 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## DataSheet(PSS-160-2)
Submersible Motor Pump Data Sheet
1 | Model | PSS-160-2_MS6-50033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 55 | m | Discharge Piece | STS304
10 | Rated Capacity | 3000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 90 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 1800 | ℓ/min | Coupling | STS304
15 | Max. Flow | 3800 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 150 | mm | Strainer | STS304
17 | Out Dia. | 215mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Sumoto |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 37 | kW | Stator Ends | Low Carbon Steel
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 96 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Spring | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 2040 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 807 | mm | Pump | 37 | kg
37 | Motor | 1170 | mm | Motor | 101 | kg
38 | Total | 1977 | mm | Total | 138 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-160-1-A | MS6-20033 | 652 |  |  | 760 |  |  | 1412
PSS-160-1 | MS6-30033 | 652 |  |  | 890 |  |  | 1542
PSS-160-2-AA | MS6-40033 | 807 |  |  | 1030 |  |  | 1837
PSS-160-2-A | MS6-50033 | 807 |  |  | 1170 |  |  | 1977
PSS-160-2 | MS6-50033 | 807 |  |  | 1170 |  |  | 1977
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-160-1-A | MS6-20033 | 31 |  |  | 54 |  |  | 85
PSS-160-1 | MS6-30033 | 31 |  |  | 70 |  |  | 101
PSS-160-2-AA | MS6-40033 | 37 |  |  | 90 |  |  | 127
PSS-160-2-A | MS6-50033 | 37 |  |  | 101 |  |  | 138
PSS-160-2 | MS6-50033 | 37 |  |  | 101 |  |  | 138
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 6" (150mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-160 Series
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  |  | MATERIAL | Q'TY
1 | Discharge |  |  |  | STS304 | 1
2 | Spring |  |  |  |  | 1
3 | Upper Retainer |  |  |  |  | 1
4 | Lower Retainer |  |  |  |  | 1
5 | O-ring |  |  |  | NBR | 1
6 | Diffuser |  |  |  | STS304 | Stages
7 | Neck Ring |  |  |  | STS304+NBR | Stages
8 | Split Cone Nut |  |  |  | STS304 | Stages
9 | Ring Of Impeller |  |  |  |  | Stages
10 | Impeller |  |  |  |  | Stages
11 | Space Washer |  |  |  | MoO2+PTFE | 1
12 | Nut for Stop Ring |  |  |  | STS304 | 1
13 | Shaft |  |  |  | STS431 | 1
14 | Screw |  |  |  | STS304 | 2
15 | Key |  |  |  |  | 2
16 | Strainer |  |  |  |  | 1
17 | Cable Guard |  |  |  |  | 1~2
18 | Valve Cup |  |  |  |  | 1
19 | Valve Seat |  |  |  |  | 1
20 | Bearing |  |  |  | NBR | Stages
21 | Spilt Cone |  |  |  | STS304 | Stages
22 | Bearing |  |  |  | NBR | 1
23 | Stop Ring |  |  |  | STS304 | 1
24 | Bottom diffuser |  |  |  |  | 1
25 | Stap |  |  |  |  | 4
26 | Coupling |  |  |  | STS304 | 1
27 | Spring Washer |  |  |  | STS304 | 4
28 | Nut |  |  |  |  | 4
29 | O-ring |  |  |  | NBR | 1
30 | Pump Base |  |  |  | STS304 | 1
| TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
| SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-160 Series