## Datasheet (17-1)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-1_MF4-1533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 10 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 15 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.1 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 3.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 343 | mm | Pump | 5 | kg
37 | Motor | 298 | mm | Motor | 11.5 | kg
38 | Total | 641 | mm | Total | 16.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-2)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-2_MF4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 22 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 33 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 6.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 403 | mm | Pump | 6.4 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 903 | mm | Total | 23.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-4)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-4_MF4-5033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 48 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 60 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS410
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 524 | mm | Pump | 9.3 | kg
37 | Motor | 600 | mm | Motor | 25 | kg
38 | Total | 1124 | mm | Total | 34.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-6)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-6_MF4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 70 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 90 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 16 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 645 | mm | Pump | 12.2 | kg
37 | Motor | 752 | mm | Motor | 31.8 | kg
38 | Total | 1397 | mm | Total | 44 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-9)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-9_MF6-10033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 105 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 130 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 19.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 9 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 827 | mm | Pump | 16.6 | kg
37 | Motor | 646 | mm | Motor | 52 | kg
38 | Total | 1473 | mm | Total | 68.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-13)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-13_MF6-15033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 150 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 220 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 28.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 13 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1069 | mm | Pump | 22.4 | kg
37 | Motor | 711 | mm | Motor | 58 | kg
38 | Total | 1780 | mm | Total | 80.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-18)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-18_MF6-20033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 200 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 270 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 15 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 37.3 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 18 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1371 | mm | Pump | 29.6 | kg
37 | Motor | 777 | mm | Motor | 64 | kg
38 | Total | 2148 | mm | Total | 93.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-22)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-22_MF6-25033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 260 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 340 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 18.5 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 46 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 22 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1613 | mm | Pump | 35.4 | kg
37 | Motor | 841 | mm | Motor | 70 | kg
38 | Total | 2454 | mm | Total | 105.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet (17-26)
Submersible Motor Pump Data Sheet
1 | Model | PSS-17-26_MF6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 310 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | STS304
11 | Shut off Head | 390 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 65 | % | Pump Shaft | STS431
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 450 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 65 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 55.4 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 26 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1855 | mm | Pump | 41.2 | kg
37 | Motor | 907 | mm | Motor | 76 | kg
38 | Total | 2762 | mm | Total | 117.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-17-1 | MF4-1512 | 343 |  |  | 345 |  |  | 688
| MF4-1533 |  |  |  | 298 |  |  | 641
PSS-17-2 | MF4-3012 | 403 |  |  | 560 |  |  | 963
| MF4-3033 |  |  |  | 500 |  |  | 903
PSS-17-3 | MF4-5033 | 464 |  |  | 600 |  |  | 1064
PSS-17-4 | MF4-5033 | 524 |  |  | 600 |  |  | 1124
PSS-17-5 | MF4-7533 | 585 |  |  | 752 |  |  | 1337
PSS-17-6 | MF4-7533 | 645 |  |  | 752 |  |  | 1397
PSS-17-7 | MF6-10033 | 706 |  |  | 646 |  |  | 1352
PSS-17-8 | MF6-10033 | 766 |  |  | 646 |  |  | 1412
PSS-17-9 | MF6-10033 | 827 |  |  | 646 |  |  | 1473
PSS-17-12 | MF6-15033 | 1008 |  |  | 711 |  |  | 1719
PSS-17-13 | MF6-15033 | 1069 |  |  | 711 |  |  | 1780
PSS-17-16 | MF6-20033 | 1250 |  |  | 777 |  |  | 2027
PSS-17-18 | MF6-20033 | 1371 |  |  | 777 |  |  | 2148
PSS-17-20 | MF6-25033 | 1492 |  |  | 841 |  |  | 2333
PSS-17-22 | MF6-25033 | 1613 |  |  | 841 |  |  | 2454
PSS-17-24 | MF6-30033 | 1734 |  |  | 907 |  |  | 2641
PSS-17-26 | MF6-30033 | 1855 |  |  | 907 |  |  | 2762
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-17-1 | MF4-1512 | 5 |  |  | 12.6 |  |  | 17.6
| MF4-1533 |  |  |  | 11.5 |  |  | 16.5
PSS-17-2 | MF4-3033 | 6.4 |  |  | 20 |  |  | 26.4
| MF4-3033 |  |  |  | 17 |  |  | 23.4
PSS-17-3 | MF4-5033 | 7.9 |  |  | 25 |  |  | 32.9
PSS-17-4 | MF4-5033 | 9.3 |  |  | 25 |  |  | 34.3
PSS-17-5 | MF4-7533 | 10.8 |  |  | 31.8 |  |  | 42.6
PSS-17-6 | MF4-7533 | 12.2 |  |  | 31.8 |  |  | 44
PSS-17-7 | MF6-10033 | 13.7 |  |  | 52 |  |  | 65.7
PSS-17-8 | MF6-10033 | 15.1 |  |  | 52 |  |  | 67.1
PSS-17-9 | MF6-10033 | 16.6 |  |  | 52 |  |  | 68.6
PSS-17-12 | MF6-15033 | 20.9 |  |  | 58 |  |  | 78.9
PSS-17-13 | MF6-15033 | 22.4 |  |  | 58 |  |  | 80.4
PSS-17-16 | MF6-20033 | 26.7 |  |  | 64 |  |  | 90.7
PSS-17-18 | MF6-20033 | 29.6 |  |  | 64 |  |  | 93.6
PSS-17-20 | MF6-25033 | 32.5 |  |  | 70 |  |  | 102.5
PSS-17-22 | MF6-25033 | 35.4 |  |  | 70 |  |  | 105.4
PSS-17-24 | MF6-30033 | 38.3 |  |  | 76 |  |  | 114.3
PSS-17-26 | MF6-30033 | 41.2 |  |  | 76 |  |  | 117.2
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 2 1/2" (65mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
145mm
P.L
M.L
T.L
Cable Guard Included
Outline Drawing
of PSS-17 Series

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge |  |  | STS304 |  | 1
2 | Valve cone |  |  | STS304 |  | 1
3 | Valve seat |  |  | STS304 |  | 1
4 | Spilt cone nut |  |  | STS304 |  | Stages
5 | Impeller |  |  | STS304
6 | Split cone |  |  | STS304
7 | Nock ring |  |  | NBR
8 | Diffuser |  |  | STS304
9 | Bearing |  |  | NBR
10 | Cunnecting piece |  |  | STS304 |  | 1
11 | Strainer |  |  | STS304 |  | 1
12 | Suction interconnector |  |  | STS304 |  | 1
13 | Pump shaft/coupling |  |  | STS431/304 |  | 1
14 | Coupling |  |  | STS304 |  | 1
15 | Strap |  |  | STS304 |  | 4
16 | Nut |  |  | STS304 |  | 4
17 | Cable Guard |  |  | STS304 |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
1
1
2
1
3
1
4
1
5
1
6
1
7
1
8
1
9
1
10
11
1
12
1
13
1
14
1
15
1
16
1
17
1
Outline Drawing
of PSS-17 Series

## Test Report(17-1)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 100 | 200 | 300 | 400 | 500 | 542
Dis. Head | (m) | 15.3 | 15.1 | 13 | 10.6 | 7.4 | 2.5 | 0.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.012871 | 0.051483 | 0.11584 | 0.20593 | 0.32177 | 0.3781
Total Head | (m) | 16.1 | 15.9129 | 13.8515 | 11.5158 | 8.4059 | 3.6218 | 1.2781
Water Power | (㎾) | 0 | 0.25938 | 0.45156 | 0.56312 | 0.54807 | 0.29517 | 0.11291
Shaft Power | (㎾) | 0.53048 | 0.66956 | 0.7448 | 0.86108 | 0.95836 | 0.99332 | 0.98268
Pump Eff. | (%) | 0 | 38.7388 | 60.6281 | 65.3975 | 57.188 | 29.7159 | 11.4905
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 1.48 | 1.71 | 1.83 | 2.04 | 2.22 | 2.29 | 2.27
Motor Input | (㎾) | 0.698 | 0.881 | 0.98 | 1.133 | 1.261 | 1.307 | 1.293
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.1 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 10 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 0.8
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 3.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | Franklin | Turbin | 30 | 29
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-1＿MF4-1533 |  | Customer |  |  |  | 0.5
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-2)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 102 | 202 | 300 | 460 | 548
Dis. Head | (m) | 30 | 29.1 | 26.8 | 22.5 | 10.5 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013391 | 0.052518 | 0.11584 | 0.27235 | 0.38652
Total Head | (m) | 32.5 | 31.6134 | 29.3525 | 25.1158 | 13.2723 | 2.8865
Water Power | (㎾) | 0 | 0.5256 | 0.96646 | 1.2282 | 0.99516 | 0.25784
Shaft Power | (㎾) | 1.1053 | 1.2737 | 1.4567 | 1.6616 | 1.852 | 1.7934
Pump Eff. | (%) | 0 | 41.2666 | 66.3468 | 73.9128 | 53.7355 | 14.3769
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.22 | 4.41 | 4.59 | 4.88 | 5.18 | 5.06
Motor Input | (㎾) | 1.51 | 1.74 | 1.99 | 2.27 | 2.53 | 2.45
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 22 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-2_MF4-3033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-4)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 102 | 202 | 300 | 450 | 530
Dis. Head | (m) | 60 | 58 | 53 | 47 | 26 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.14234 | 0.56092 | 1.2621 | 2.2157 | 3.5057
Total Head | (m) | 61 | 59.1423 | 54.5609 | 49.2621 | 29.2157 | 4.5057
Water Power | (㎾) | 0 | 0.94779 | 1.7359 | 2.2792 | 2.24 | 1.0762
Shaft Power | (㎾) | 1.9447 | 2.4882 | 3.1436 | 3.6307 | 3.8422 | 3.6137
Pump Eff. | (%) | 0 | 38.0921 | 55.2207 | 62.7758 | 58.3004 | 29.7801
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 6.59 | 7.2 | 8.1 | 8.86 | 9.21 | 8.85
Motor Input | (㎾) | 2.519 | 3.223 | 4.072 | 4.703 | 4.977 | 4.681
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 48 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-4_MF4-5033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-6)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 102 | 200 | 301 | 336 | 373 | 400 | 533
Dis. Head | (m) | 90 | 88 | 85 | 75 | 70 | 60 | 51 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013391 | 0.051483 | 0.11661 | 0.14531 | 0.17907 | 0.20593 | 0.36565
Total Head | (m) | 91 | 89.0134 | 86.0515 | 76.1166 | 71.1453 | 61.1791 | 52.2059 | 2.3656
Water Power | (㎾) | 0 | 1.4799 | 2.8053 | 3.7345 | 3.8965 | 3.7196 | 3.4038 | 0.20552
Shaft Power | (㎾) | 3.5424 | 4.3542 | 5.2 | 5.6425 | 5.6536 | 5.5929 | 5.4908 | 4.497
Pump Eff. | (%) | 0 | 33.989 | 53.9479 | 66.1854 | 68.9204 | 66.506 | 61.9915 | 4.5703
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 9.92 | 11.16 | 12.67 | 13.52 | 13.55 | 13.4 | 13.23 | 11.45
Motor Input | (㎾) | 4.787 | 5.884 | 7.027 | 7.625 | 7.64 | 7.558 | 7.42 | 6.077
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 70 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 16 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin | 49 | 26
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-6_MF4-7533 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-9)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 107 | 206 | 304 | 308 | 406 | 565
Dis. Head | (m) | 134.5 | 132 | 125 | 107.5 | 106 | 77.5 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014736 | 0.054619 | 0.11895 | 0.1221 | 0.21216 | 0.41087
Total Head | (m) | 137 | 134.5147 | 127.5546 | 110.1189 | 108.6221 | 80.2122 | 2.9109
Water Power | (㎾) | 0 | 2.3461 | 4.283 | 5.4566 | 5.4533 | 5.3083 | 0.26808
Shaft Power | (㎾) | 5.0154 | 5.811 | 6.8094 | 7.6518 | 7.683 | 8.2212 | 7.4724
Pump Eff. | (%) | 0 | 40.3729 | 62.8988 | 71.3115 | 70.9783 | 64.5682 | 3.5876
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 13.44 | 14.72 | 16.45 | 18.01 | 18.06 | 19.11 | 17.72
Motor Input | (㎾) | 6.43 | 7.45 | 8.73 | 9.81 | 9.85 | 10.54 | 9.58
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 105 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | FRANKLIN | Turbin | 12
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-9_MF6-10033 |  | Customer |  |  |  | 2 |  | 2008.02.20
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-13)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 101 | 208 | 302 | 330 | 402 | 540
Dis. Head | (m) | 229 | 209 | 196 | 160 | 150 | 102 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01313 | 0.055684 | 0.11739 | 0.14016 | 0.208 | 0.37531
Total Head | (m) | 231.5 | 211.5131 | 198.5557 | 162.6174 | 152.6402 | 104.708 | 3.8753
Water Power | (㎾) | 0 | 3.4821 | 6.7318 | 8.005 | 8.2105 | 6.8611 | 0.34111
Shaft Power | (㎾) | 7.4971 | 9.0546 | 11.1157 | 11.9578 | 11.9498 | 11.5969 | 9.4075
Pump Eff. | (%) | 0 | 38.4572 | 60.5614 | 66.9437 | 68.7084 | 59.1631 | 3.6259
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 19.41 | 21.9 | 25.6 | 27.15 | 27.14 | 26.46 | 22.47
Motor Input | (㎾) | 9.348 | 11.29 | 13.86 | 14.91 | 14.9 | 14.46 | 11.73
Motor Eff. | (%) | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 150 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 28.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80.2 | Maker | FRANKLIN | Turbin | 24 | 24
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-13_MF6-15033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-18)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 135 | 260 | 320 | 390 | 420 | 490
Dis. Head | (m) | 280 | 270 | 220 | 200 | 142 | 92 | 20
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023457 | 0.087007 | 0.1318 | 0.19576 | 0.22704 | 0.30903
Total Head | (m) | 281.5 | 271.5235 | 221.587 | 201.6318 | 143.6958 | 93.727 | 21.809
Water Power | (㎾) | 0 | 5.9749 | 9.3909 | 10.5171 | 9.1347 | 6.4166 | 1.7419
Shaft Power | (㎾) | 9.6288 | 13.056 | 15.1776 | 15.0144 | 14.4432 | 13.6272 | 11.9952
Pump Eff. | (%) | 0 | 45.7634 | 61.8731 | 70.0469 | 63.246 | 47.0864 | 14.5215
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 25 | 30.2 | 33.7 | 33.6 | 32.5 | 31.1 | 28.6
Motor Input | (㎾) | 11.8 | 16 | 18.6 | 18.4 | 17.7 | 16.7 | 14.7
Motor Eff. | (%) | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 15 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 200 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 1.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 37.3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 81.6 | Maker | FRANKLIN | Turbin | 19.5 | 19.5
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-18_MF6-20033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-22)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 100 | 214 | 320 | 420 | 519 | 563
Dis. Head | (m) | 335 | 334 | 312 | 257 | 183 | 75 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.012871 | 0.058943 | 0.1318 | 0.22704 | 0.34669 | 0.40796
Total Head | (m) | 338 | 337.0129 | 315.0589 | 260.1318 | 186.227 | 78.3467 | 4.408
Water Power | (㎾) | 0 | 5.4933 | 10.9899 | 13.5685 | 12.7491 | 6.6279 | 0.40451
Shaft Power | (㎾) | 13.448 | 15.252 | 18.368 | 20.418 | 21.402 | 20.664 | 19.352
Pump Eff. | (%) | 0 | 36.017 | 59.8317 | 66.4535 | 59.5697 | 32.0746 | 2.0903
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 32 | 34 | 40 | 43 | 45 | 43 | 41
Motor Input | (㎾) | 16.4 | 18.6 | 22.4 | 24.9 | 26.1 | 25.2 | 23.6
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 18.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 260 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 3
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 46 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | FRANKLIN | Turbin | 6
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-22_MF6-25033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(17-26)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 210 | 310 | 397 | 496 | 562
Dis. Head | (m) | 395 | 370 | 317 | 240 | 125 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.05676 | 0.12369 | 0.20286 | 0.31664 | 0.40652
Total Head | (m) | 397.5 | 372.5568 | 319.6237 | 242.7029 | 127.8166 | 3.9065
Water Power | (㎾) | 0 | 12.7526 | 16.1506 | 15.7055 | 10.3337 | 0.35786
Shaft Power | (㎾) | 15.023 | 20.916 | 23.24 | 24.9 | 24.236 | 22.493
Pump Eff. | (%) | 0 | 60.9706 | 69.4948 | 63.0745 | 42.6379 | 1.591
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 34 | 42 | 48 | 51 | 50 | 47
Motor Input | (㎾) | 18.1 | 25.2 | 28 | 30 | 29.2 | 27.1
Motor Eff. | (%) | 83 | 83 | 83 | 83 | 83 | 83
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 310 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 65 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 55.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 83 | Maker | FRANKLIN | Turbin | 6
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-17-26_MF6-30033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification