## Datasheet(2-9)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-2-9_MF4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 55 | m | Discharge Piece | STS304
10 | Rated Capacity | 30 | ℓ/min | Impeller | STS304
11 | Shut off Head | 77 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 55 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 50 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 2.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 9 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 356 | mm | Pump | 3 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 654 | mm | Total | 13.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(2-15)
Submersible Motor Pump Data Sheet
1 | Model | PSS-2-15_MF4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 100 | m | Discharge Piece | STS304
10 | Rated Capacity | 30 | ℓ/min | Impeller | STS304
11 | Shut off Head | 125 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 55 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 50 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 9.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 15 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 482 | mm | Pump | 4.2 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 780 | mm | Total | 15.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(2-27)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-2-27_MF4-2012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 170 | m | Discharge Piece | STS304
10 | Rated Capacity | 30 | ℓ/min | Impeller | STS304
11 | Shut off Head | 225 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 50 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 13.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 27 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 734 | mm | Pump | 6.4 | kg
37 | Motor | 384 | mm | Motor | 14.5 | kg
38 | Total | 1118 | mm | Total | 20.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(2-27)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-2-27_MF4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 170 | m | Discharge Piece | STS304
10 | Rated Capacity | 30 | ℓ/min | Impeller | STS304
11 | Shut off Head | 225 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 50 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 4.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 27 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 734 | mm | Pump | 6.4 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 1080 | mm | Total | 19.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(2-34)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-2-34_MF4-3012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 220 | m | Discharge Piece | STS304
10 | Rated Capacity | 30 | ℓ/min | Impeller | STS304
11 | Shut off Head | 285 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 50 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 17 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 34 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 904 | mm | Pump | 10 | kg
37 | Motor | 560 | mm | Motor | 20 | kg
38 | Total | 1464 | mm | Total | 30 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(2-34)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-2-34_MF4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 220 | m | Discharge Piece | STS304
10 | Rated Capacity | 30 | ℓ/min | Impeller | STS304
11 | Shut off Head | 285 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 20 | ℓ/min | Coupling | STS304
15 | Max. Flow | 50 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 6.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 34 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 904 | mm | Pump | 10 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 1404 | mm | Total | 27 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PSS-2-9 | MF4-1012 | 9 |  |  | 1 |  | 1 | 220 | 60
| MF4-1033 | [5 empty] | 3 | 380
PSS-2-12 | MF4-1012 | 12 |  |  | 1 |  | 1 | 220
| MF4-1033 | [5 empty] | 3 | 380
PSS-2-15 | MF4-1012 | 15 |  |  | 1 |  | 1 | 220
| MF4-1033 | [5 empty] | 3 | 380
PSS-2-21 | MF4-1512 | 21 |  |  | 1.5 |  | 1 | 220
| MF4-1533 | [5 empty] | 3 | 380
PSS-2-27 | MF4-2012 | 27 |  |  | 2 |  | 1 | 220
| MF4-2033 | [5 empty] | 3 | 380
PSS-2-34 | MF4-3012 | 34 |  |  | 3 |  | 1 | 220
| MF4-3033 | [5 empty] | 3 | 380
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-2-9 | MF4-1012 | 356 |  |  | 298 |  |  | 654
| MF4-1033 | 356 |  |  | 298 |  |  | 654
PSS-2-12 | MF4-1012 | 419 |  |  | 298 |  |  | 717
| MF4-1033 | 419 |  |  | 298 |  |  | 717
PSS-2-15 | MF4-1012 | 482 |  |  | 298 |  |  | 780
| MF4-1033 | 482 |  |  | 298 |  |  | 780
PSS-2-21 | MF4-1512 | 608 |  |  | 345 |  |  | 953
| MF4-1533 | 608 |  |  | 298 |  |  | 906
PSS-2-27 | MF4-2012 | 734 |  |  | 384 |  |  | 1118
| MF4-2033 | 734 |  |  | 346 |  |  | 1080
PSS-2-34 | MF4-3012 | 904 |  |  | 560 |  |  | 1464
| MF4-3033 | 904 |  |  | 500 |  |  | 1404
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-2-9 | MF4-1012 | 3 |  |  | 10.9 |  |  | 13.9
| MF4-1033 |  |  |  | 10.9 |  |  | 13.9
PSS-2-12 | MF4-1012 | 3.6 |  |  | 10.9 |  |  | 14.5
| MF4-1033 |  |  |  | 10.9 |  |  | 14.5
PSS-2-15 | MF4-1012 | 4.2 |  |  | 10.9 |  |  | 15.1
| MF4-1033 |  |  |  | 10.9 |  |  | 15.1
PSS-2-21 | MF4-1512 | 5.3 |  |  | 12.6 |  |  | 17.9
| MF4-1533 |  |  |  | 11.5 |  |  | 16.8
PSS-2-27 | MF4-1512 | 6.4 |  |  | 14.5 |  |  | 20.9
| MF4-1533 |  |  |  | 13.1 |  |  | 19.5
PSS-2-34 | MF4-3012 | 10 |  |  | 20 |  |  | 30
| MF4-3033 |  |  |  | 17 |  |  | 27
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 1 1/4" (32mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-2 Series
98mm
P.L
M.L
T.L
P.L
M.L
T.L
Cable Guard Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge piece |  |  | STS304 |  | 1
2 | Screw |  |  | - |  | 1
3 | Valve guide |  |  | - |  | 1
4 | Valve cone |  |  | STS304 |  | 1
5 | Valve seat |  |  | NBR |  | 1
6 | Valve casing |  |  | STS304 |  | 1
7 | Stop ring |  |  |  |  | 1
8 | Lock nut |  |  |  |  | 1
9 | Stop ring washer |  |  |  |  | 1
10 | Impeller |  |  |  |  | Stages
11 | Neck ring |  |  | NBR |  | Stages
12 | Bearing |  |  |  |  | Stages
13 | Diffuser |  |  | STS304 |  | Stages
14 | Spacer |  |  | - |  | 1
15 | Pump shaft/coupling |  |  | STS431/304 |  | 1
16 | Strainer |  |  | STS304 |  | 1
17 | Suction interconnector |  |  |  |  | 1
18 | Screw |  |  | - |  | 4
19 | Washer |  |  | STS304 |  | 4
20 | Strap |  |  |  |  | 4
21 | Cable GUARD |  |  |  |  | 1
22 | Check valve |  |  | - |  | 1
23 | Diffuseer Assy |  |  | - |  | Stages
24 | Strainer Assy |  |  | - |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-2 Series

## Test Report(2-9)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 15 | 30 | 45 | 60 | 66
Dis. Head | (m) | 77.9 | 74.1 | 63.9 | 44 | 12 | 0.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0049299 | 0.01972 | 0.044369 | 0.078879 | 0.095444
Total Head | (m) | 78.9 | 75.1049 | 64.9197 | 45.0444 | 13.0789 | 1.1954
Water Power | (㎾) | 0 | 0.18363 | 0.31746 | 0.3304 | 0.12791 | 0.012861
Shaft Power | (㎾) | 0.3885 | 0.5523 | 0.6685 | 0.7245 | 0.6741 | 0.6678
Pump Eff. | (%) | 0 | 33.2485 | 47.488 | 45.6039 | 18.9751 | 1.9258
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 1.84 | 1.99 | 2.14 | 2.24 | 2.17 | 2.15
Motor Input | (㎾) | 0.555 | 0.789 | 0.955 | 1.035 | 0.963 | 0.954
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 30 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 55 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 2.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | Franklin | Turbin | 17 | 18
Item No. |  |  | Serial No. |  | Inspector | I.H.GO | Run (Hr) | B/R (℃) | Test Date
Model | PSS-2-9＿MF4-1033 |  | Customer |  |  |  | 0.5 |  | 2014.02.21
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(2-15)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 15 | 30 | 42.4 | 45.6 | 50 | 65.5
Dis. Head | (m) | 127.5 | 122 | 104 | 80 | 71 | 55 | 0.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0049299 | 0.01972 | 0.03939 | 0.045561 | 0.054777 | 0.094003
Total Head | (m) | 128.5 | 123.0049 | 105.0197 | 81.0394 | 72.0456 | 56.0548 | 1.594
Water Power | (㎾) | 0 | 0.30075 | 0.51355 | 0.56008 | 0.5355 | 0.45685 | 0.017018
Shaft Power | (㎾) | 0.47642 | 0.69569 | 0.89601 | 0.99015 | 0.99359 | 0.97867 | 0.88396
Pump Eff. | (%) | 0 | 43.2302 | 57.3146 | 56.5651 | 53.8953 | 46.6803 | 1.9252
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.67 | 7.7 | 8.9 | 9.54 | 9.57 | 9.46 | 8.82
Motor Input | (㎾) | 0.83 | 1.212 | 1.561 | 1.725 | 1.731 | 1.705 | 1.54
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 30 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 100 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | FRANKLIN | Turbin | 29
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-2-15_MF4-1012 |  | Customer |  |  |  | 2 |  | 06/04/12
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(2-27)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 10 | 20.2 | 30.5 | 40 | 42 | 50.3 | 61.4
Dis. Head | (m) | 230 | 222 | 205 | 175 | 130 | 120 | 70 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0021911 | 0.0089405 | 0.020383 | 0.035057 | 0.038651 | 0.055436 | 0.082603
Total Head | (m) | 231 | 223.0022 | 206.0089 | 176.0204 | 131.0351 | 121.0387 | 71.0554 | 3.0826
Water Power | (㎾) | 0 | 0.36349 | 0.67831 | 0.87509 | 0.85435 | 0.82863 | 0.58258 | 0.030851
Shaft Power | (㎾) | 0.88477 | 1.1655 | 1.4565 | 1.7344 | 1.8769 | 1.8865 | 1.8445 | 1.8308
Pump Eff. | (%) | 0 | 31.1885 | 46.571 | 50.4532 | 45.52 | 43.9243 | 31.584 | 1.6852
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.37 | 8.08 | 9.91 | 11.78 | 12.78 | 12.79 | 12.44 | 12.35
Motor Input | (㎾) | 1.286 | 1.694 | 2.117 | 2.521 | 2.728 | 2.742 | 2.681 | 2.661
Motor Eff. | (%) | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 30 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 170 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 13.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68.8 | Maker | FRANKLIN | Turbin | 54 | 33
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-2-27_MF4-2012 |  | Customer |  |  |  | 2 |  | 2006.09.06
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(2-27)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 10 | 20 | 30.2 | 40.1 | 42.2 | 50 | 61.7
Dis. Head | (m) | 231 | 223 | 205 | 177 | 132 | 120 | 72 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0021911 | 0.0087643 | 0.019984 | 0.035233 | 0.03902 | 0.054777 | 0.083412
Total Head | (m) | 232 | 224.0022 | 206.0088 | 178.02 | 133.0352 | 121.039 | 73.0548 | 2.0834
Water Power | (㎾) | 0 | 0.36512 | 0.67159 | 0.87632 | 0.86956 | 0.83258 | 0.5954 | 0.020953
Shaft Power | (㎾) | 0.84924 | 1.1209 | 1.3655 | 1.5812 | 1.6917 | 1.7005 | 1.6715 | 1.6668
Pump Eff. | (%) | 0 | 32.5752 | 49.1817 | 55.4211 | 51.4002 | 48.9608 | 35.6201 | 1.2571
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.12 | 3.5 | 3.9 | 4.3 | 4.52 | 4.53 | 4.47 | 4.46
Motor Input | (㎾) | 1.26 | 1.663 | 2.026 | 2.346 | 2.51 | 2.523 | 2.48 | 2.473
Motor Eff. | (%) | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 30 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 170 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 67.4 | Maker | FRANKLIN | Turbin | 43 | 28
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-2-27_MF4-2033 |  | Customer |  |  |  | 2 |  | 06/09/04
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(2-34)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 10.1 | 20.3 | 30.1 | 40 | 45.2 | 50.2 | 63.2
Dis. Head | (m) | 296 | 289 | 266 | 234 | 179 | 140 | 99 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0022351 | 0.0090292 | 0.019851 | 0.035057 | 0.044765 | 0.055216 | 0.087517
Total Head | (m) | 297 | 290.0022 | 267.009 | 235.0199 | 180.0351 | 141.0448 | 100.0552 | 4.0875
Water Power | (㎾) | 0 | 0.47743 | 0.88351 | 1.1531 | 1.1738 | 1.0392 | 0.81871 | 0.042108
Shaft Power | (㎾) | 1.1746 | 1.5456 | 1.8844 | 2.1889 | 2.3478 | 2.3555 | 2.31 | 2.2533
Pump Eff. | (%) | 0 | 30.8897 | 46.8853 | 52.6784 | 49.997 | 44.1164 | 35.4421 | 1.8687
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 8.37 | 10.56 | 12.69 | 14.71 | 15.67 | 15.72 | 15.44 | 15.01
Motor Input | (㎾) | 1.678 | 2.208 | 2.692 | 3.127 | 3.354 | 3.365 | 3.3 | 3.219
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 30 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 220 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 17.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | FRANKLIN | Turbin | 45 | 26
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-2-34_MF4-3012 |  | Customer |  |  |  | 2 |  | 2006.09.11
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(2-34)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 10.5 | 20.5 | 30.6 | 40.2 | 44.4 | 50 | 62.4
Dis. Head | (m) | 290 | 285 | 260 | 225 | 170 | 140 | 95 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0024157 | 0.009208 | 0.020516 | 0.035409 | 0.043194 | 0.054777 | 0.085316
Total Head | (m) | 291 | 286.0024 | 261.0092 | 226.0205 | 171.0354 | 141.0432 | 96.0548 | 4.0853
Water Power | (㎾) | 0 | 0.48949 | 0.87216 | 1.1273 | 1.1207 | 1.0208 | 0.78285 | 0.041553
Shaft Power | (㎾) | 1.1807 | 1.5562 | 1.8739 | 2.1506 | 2.2677 | 2.3065 | 2.2304 | 2.1814
Pump Eff. | (%) | 0 | 31.4537 | 46.5421 | 52.4196 | 49.4205 | 44.2551 | 35.0989 | 1.9049
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.02 | 4.47 | 4.97 | 5.45 | 5.64 | 5.72 | 5.56 | 5.49
Motor Input | (㎾) | 1.613 | 2.126 | 2.56 | 2.938 | 3.098 | 3.151 | 3.047 | 2.98
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 30 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 220 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin | 58 | 43
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-2-34_MF4-3033 |  | Customer |  |  |  | 2 |  | 06/09/04
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification