## Datasheet(5-4)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-4_MF4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 24 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 34 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 120 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 9.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 251 | mm | Pump | 2 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 549 | mm | Total | 12.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-4)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-4_MF4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 24 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 34 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 120 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kW | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 2.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 251 | mm | Pump | 2 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 549 | mm | Total | 12.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-5)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-5_MF4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 31 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 44 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 9.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 272 | mm | Pump | 2.2 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 570 | mm | Total | 13.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-5)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-5_MF4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 31 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 44 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kW | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 2.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 272 | mm | Pump | 2.2 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 570 | mm | Total | 13.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-7)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-7_MF4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 45 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 62 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 9.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 314 | mm | Pump | 2.6 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 612 | mm | Total | 13.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-7)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-7_MF4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 45 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 62 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kW | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 2.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 314 | mm | Pump | 2.6 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 612 | mm | Total | 13.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-9)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-9_MF4-1512 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 57 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 80 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.1 | kW | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 11.5 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 9 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 356 | mm | Pump | 3 | kg
37 | Motor | 345 | mm | Motor | 12.6 | kg
38 | Total | 701 | mm | Total | 15.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-9)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-9_MF4-1533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 57 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 80 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.1 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 3.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 9 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 356 | mm | Pump | 3 | kg
37 | Motor | 298 | mm | Motor | 11.5 | kg
38 | Total | 654 | mm | Total | 14.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-11)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-11_MF4-2012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 70 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 98 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 13.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 11 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 398 | mm | Pump | 3.4 | kg
37 | Motor | 384 | mm | Motor | 14.5 | kg
38 | Total | 782 | mm | Total | 17.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-11)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-11_MF4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 70 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 98 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 4.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 11 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 398 | mm | Pump | 3.4 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 744 | mm | Total | 16.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-15)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-15_MF4-3012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 100 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 135 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 17 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 15 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 482 | mm | Pump | 4.1 | kg
37 | Motor | 560 | mm | Motor | 20 | kg
38 | Total | 1042 | mm | Total | 24.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-15)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-15_MF4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 100 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 135 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 6.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 15 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 482 | mm | Pump | 4.1 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 982 | mm | Total | 21.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-26)
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-26_MF4-5033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 170 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 230 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS410
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 26 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 713 | mm | Pump | 6.2 | kg
37 | Motor | 600 | mm | Motor | 25 | kg
38 | Total | 1313 | mm | Total | 31.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-39)
Submersible Motor Pump Data Sheet
1 | Model | PSS-5-39_MF4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 260 | m | Discharge Piece | STS304
10 | Rated Capacity | 80 | ℓ/min | Impeller | STS304
11 | Shut off Head | 350 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 40 | ℓ/min | Coupling | STS304
15 | Max. Flow | 140 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 16 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 39 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 994 | mm | Pump | 11.1 | kg
37 | Motor | 752 | mm | Motor | 31.8 | kg
38 | Total | 1746 | mm | Total | 42.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PSS-5-4 | MF4-1012 | 4 |  |  | 1 |  | 1 | 220 | 60
| MF4-1033 | [5 empty] | 3 | 380
PSS-5-5 | MF4-1012 | 5 |  |  | 1 |  | 1 | 220
| MF4-1033 | [5 empty] | 3 | 380
PSS-5-7 | MF4-1012 | 7 |  |  | 1 |  | 1 | 220
| MF4-1033 | [5 empty] | 3 | 380
PSS-5-9 | MF4-1512 | 9 |  |  | 1.5 |  | 1 | 220
| MF4-1533 | [5 empty] | 3 | 380
PSS-5-11 | MF4-2012 | 11 |  |  | 2 |  | 1 | 220
| MF4-2033 | [5 empty] | 3 | 380
PSS-5-15 | MF4-3012 | 15 |  |  | 3 |  | 1 | 220
| MF4-3033 | [5 empty] | 3 | 380
PSS-5-21 | MF4-5033 | 21 |  |  | 5 |  | 3 | 380
PSS-5-26 | MF4-5033 | 26 |  |  | 5 |  | 3 | 380
PSS-5-39 | MF4-7533 | 39 |  |  | 7.5 |  | 3 | 380
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-5-4 | MF4-1012 | 251 |  |  | 298 |  |  | 549
| MF4-1033 | 251 |  |  | 298 |  |  | 549
PSS-5-5 | MF4-1012 | 272 |  |  | 298 |  |  | 570
| MF4-1033 | 272 |  |  | 298 |  |  | 570
PSS-5-7 | MF4-1012 | 314 |  |  | 298 |  |  | 612
| MF4-1033 | 314 |  |  | 298 |  |  | 612
PSS-5-9 | MF4-1512 | 356 |  |  | 345 |  |  | 701
| MF4-1533 | 356 |  |  | 298 |  |  | 654
PSS-5-11 | MF4-2012 | 398 |  |  | 384 |  |  | 782
| MF4-2033 | 398 |  |  | 346 |  |  | 744
PSS-5-15 | MF4-3012 | 482 |  |  | 560 |  |  | 1042
| MF4-3033 | 482 |  |  | 500 |  |  | 982
PSS-5-21 | MF4-5033 | 608 |  |  | 600 |  |  | 1208
PSS-5-26 | MF4-5033 | 713 |  |  | 600 |  |  | 1313
PSS-5-39 | MF4-7533 | 994 |  |  | 752 |  |  | 1746
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-5-4 | MF4-1012 | 2 |  |  | 10.9 |  |  | 12.9
| MF4-1033 |  |  |  | 10.9 |  |  | 12.9
PSS-5-5 | MF4-1012 | 2.2 |  |  | 10.9 |  |  | 13.1
| MF4-1033 |  |  |  | 10.9 |  |  | 13.1
PSS-5-7 | MF4-1012 | 2.6 |  |  | 10.9 |  |  | 13.5
| MF4-1033 |  |  |  | 10.9 |  |  | 13.5
PSS-5-9 | MF4-1512 | 3 |  |  | 12.6 |  |  | 15.6
| MF4-1533 |  |  |  | 11.5 |  |  | 14.5
PSS-5-11 | MF4-2012 | 3.4 |  |  | 14.5 |  |  | 17.9
| MF4-2033 |  |  |  | 13.1 |  |  | 16.5
PSS-5-15 | MF4-3012 | 4.1 |  |  | 20 |  |  | 24.1
| MF4-3033 |  |  |  | 17 |  |  | 21.1
PSS-5-21 | MF4-5033 | 5.3 |  |  | 25 |  |  | 30.3
PSS-5-26 | MF4-5033 | 6.2 |  |  | 25 |  |  | 31.2
PSS-5-39 | MF4-7533 | 11.1 |  |  | 31.8 |  |  | 42.9
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 1 1/2" (40mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-5 Series
98mm
P.L
M.L
T.L
P.L
M.L
T.L
Cable Guard Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge piece |  |  | STS304 |  | 1
2 | Screw |  |  | - |  | 1
3 | Valve guide |  |  | - |  | 1
4 | Valve cone |  |  | STS304 |  | 1
5 | Valve seat |  |  | NBR |  | 1
6 | Valve casing |  |  | STS304 |  | 1
7 | Stop ring |  |  |  |  | 1
8 | Lock nut |  |  |  |  | 1
9 | Stop ring washer |  |  |  |  | 1
10 | Impeller |  |  |  |  | Stages
11 | Neck ring |  |  | NBR |  | Stages
12 | Bearing |  |  |  |  | Stages
13 | Diffuser |  |  | STS304 |  | Stages
14 | Spacer |  |  | - |  | 1
15 | Pump shaft/coupling |  |  | *STS431/304 |  | 1
16 | Strainer |  |  | STS304 |  | 1
17 | Suction interconnector |  |  |  |  | 1
18 | Screw |  |  | - |  | 4
19 | Washer |  |  | STS304 |  | 4
20 | Strap |  |  |  |  | 4
21 | Cable GUARD |  |  |  |  | 1
22 | Check valve |  |  | - |  | 1
23 | Diffuseer Assy |  |  | - |  | Stages
24 | Strainer Assy |  |  | - |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-5 Series

## Test Report(5-4)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 25 | 50 | 75 | 100 | 125 | 152
Dis. Head | (m) | 35.8 | 33.1 | 30.9 | 27.1 | 21 | 12.9 | 0.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0056092 | 0.022437 | 0.050483 | 0.089747 | 0.14023 | 0.20735
Total Head | (m) | 36.6 | 33.9056 | 31.7224 | 27.9505 | 21.8897 | 13.8402 | 1.1074
Water Power | (㎾) | 0 | 0.13817 | 0.25854 | 0.34169 | 0.3568 | 0.28199 | 0.027436
Shaft Power | (㎾) | 0.3025 | 0.40352 | 0.50397 | 0.57457 | 0.60787 | 0.60614 | 0.56195
Pump Eff. | (%) | 0 | 34.2399 | 51.3 | 59.4692 | 58.6976 | 46.5227 | 4.8823
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.24 | 6.4 | 6.74 | 7.07 | 7.24 | 7.24 | 7.03
Motor Input | (㎾) | 0.527 | 0.703 | 0.878 | 1.001 | 1.059 | 1.056 | 0.979
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 24 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 0.8
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | Franklin | Turbin | 31 | 31
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-4＿MF4-1012 |  | Customer |  |  |  | 0.5
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-4)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.7 | 60.4 | 101.8 | 112 | 130.6 | 167.8
Dis. Head | (m) | 34 | 31 | 28 | 20 | 18 | 11 | 0.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0084586 | 0.032741 | 0.093007 | 0.11258 | 0.15308 | 0.2527
Total Head | (m) | 34.5 | 31.5085 | 28.5327 | 20.593 | 18.6126 | 11.6531 | 1.2527
Water Power | (㎾) | 0 | 0.15767 | 0.28091 | 0.34171 | 0.33979 | 0.24807 | 0.034263
Shaft Power | (㎾) | 0.3241 | 0.4746 | 0.5992 | 0.7042 | 0.7091 | 0.6951 | 0.6636
Pump Eff. | (%) | 0 | 33.222 | 46.8809 | 48.5243 | 47.9187 | 35.6882 | 5.1632
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 1.85 | 1.96 | 2.08 | 2.23 | 2.23 | 2.21 | 2.18
Motor Input | (㎾) | 0.463 | 0.678 | 0.856 | 1.006 | 1.013 | 0.993 | 0.948
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 24 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 2.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-4_MF4-1033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-5)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.7 | 60.4 | 101.8 | 112 | 130.6 | 167.8
Dis. Head | (m) | 44 | 42 | 38 | 28 | 25 | 18 | 0.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0084586 | 0.032741 | 0.093007 | 0.11258 | 0.15308 | 0.2527
Total Head | (m) | 45 | 43.0085 | 39.0327 | 29.093 | 26.1126 | 19.1531 | 1.7527
Water Power | (㎾) | 0 | 0.21522 | 0.38429 | 0.48275 | 0.47671 | 0.40773 | 0.047939
Shaft Power | (㎾) | 0.40926 | 0.63025 | 0.84378 | 1.0125 | 1.0177 | 1.0051 | 0.9184
Pump Eff. | (%) | 0 | 34.148 | 45.5433 | 47.6775 | 46.8419 | 40.5668 | 5.2198
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.43 | 7.33 | 8.59 | 9.72 | 9.74 | 9.65 | 9.04
Motor Input | (㎾) | 0.713 | 1.098 | 1.47 | 1.764 | 1.773 | 1.751 | 1.6
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 31 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | FRANKLIN | Turbin | 28
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-5_MF4-1012 |  | Customer |  |  |  | 2 |  | 06/04/13
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-5)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.7 | 60.4 | 101.8 | 112 | 130.6 | 167.8
Dis. Head | (m) | 44 | 42 | 38 | 28 | 25 | 18 | 0.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0084586 | 0.032741 | 0.093007 | 0.11258 | 0.15308 | 0.2527
Total Head | (m) | 44.5 | 42.5085 | 38.5327 | 28.593 | 25.6126 | 18.6531 | 1.2527
Water Power | (㎾) | 0 | 0.21272 | 0.37936 | 0.47446 | 0.46758 | 0.39708 | 0.034263
Shaft Power | (㎾) | 0.3241 | 0.7546 | 0.8792 | 0.9142 | 0.9191 | 0.9051 | 0.6636
Pump Eff. | (%) | 0 | 28.1893 | 43.1486 | 51.8984 | 50.874 | 43.8717 | 5.1632
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 1.85 | 1.96 | 2.08 | 2.23 | 2.23 | 2.21 | 2.18
Motor Input | (㎾) | 0.463 | 1.078 | 1.256 | 1.306 | 1.313 | 1.293 | 0.948
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 31 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 2.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-5_MF4-1033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-7)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.7 | 60.4 | 101.8 | 112 | 130.6 | 167.8
Dis. Head | (m) | 64.1 | 58.5 | 53 | 40 | 35 | 25.5 | 0.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0084586 | 0.032741 | 0.093007 | 0.11258 | 0.15308 | 0.2527
Total Head | (m) | 65.1 | 59.5085 | 54.0327 | 41.093 | 36.1126 | 26.6531 | 1.7527
Water Power | (㎾) | 0 | 0.29779 | 0.53196 | 0.68187 | 0.65927 | 0.56739 | 0.047939
Shaft Power | (㎾) | 0.40926 | 0.63025 | 0.84378 | 1.0125 | 1.0177 | 1.0051 | 0.9184
Pump Eff. | (%) | 0 | 47.2488 | 63.0452 | 67.3431 | 64.7804 | 56.4521 | 5.2198
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.43 | 7.33 | 8.59 | 9.72 | 9.74 | 9.65 | 9.04
Motor Input | (㎾) | 0.713 | 1.098 | 1.47 | 1.764 | 1.773 | 1.751 | 1.6
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 45 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | FRANKLIN | Turbin | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-7_MF4-1012 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-7)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.7 | 60.4 | 101.8 | 112 | 130.6 | 167.8
Dis. Head | (m) | 64.1 | 58.5 | 53 | 40 | 35 | 25.5 | 0.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0084586 | 0.032741 | 0.093007 | 0.11258 | 0.15308 | 0.2527
Total Head | (m) | 64.6 | 59.0085 | 53.5327 | 40.593 | 35.6126 | 26.1531 | 1.2527
Water Power | (㎾) | 0 | 0.29528 | 0.52704 | 0.67358 | 0.65014 | 0.55674 | 0.034263
Shaft Power | (㎾) | 0.3241 | 0.8946 | 1.0192 | 1.0542 | 1.0591 | 1.0451 | 0.7336
Pump Eff. | (%) | 0 | 33.0074 | 51.7112 | 63.8945 | 61.3864 | 53.2716 | 4.6705
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 1.85 | 1.96 | 2.08 | 2.23 | 2.23 | 2.21 | 2.18
Motor Input | (㎾) | 0.463 | 1.278 | 1.456 | 1.506 | 1.513 | 1.493 | 1.048
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 45 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 2.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-7_MF4-1033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-9)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.7 | 60.4 | 101.8 | 112 | 130.6 | 167.8
Dis. Head | (m) | 80 | 77 | 65 | 49 | 45 | 30 | 0.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0084586 | 0.032741 | 0.093007 | 0.11258 | 0.15308 | 0.2527
Total Head | (m) | 81 | 78.0085 | 66.0327 | 50.093 | 46.1126 | 31.1531 | 1.7527
Water Power | (㎾) | 0 | 0.39036 | 0.65011 | 0.83121 | 0.84183 | 0.66318 | 0.047939
Shaft Power | (㎾) | 0.54188 | 0.83448 | 1.1172 | 1.3406 | 1.3475 | 1.3308 | 1.216
Pump Eff. | (%) | 0 | 46.7791 | 58.1906 | 62.0012 | 62.4745 | 49.8347 | 3.9423
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.43 | 7.33 | 8.59 | 9.72 | 9.74 | 9.65 | 9.04
Motor Input | (㎾) | 0.713 | 1.098 | 1.47 | 1.764 | 1.773 | 1.751 | 1.6
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.1 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 57 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 11.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | FRANKLIN | Turbin | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-9_MF4-1512 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-9)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.7 | 60.4 | 101.8 | 112 | 130.6 | 167.8
Dis. Head | (m) | 80 | 77 | 65 | 49 | 45 | 30 | 0.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0084586 | 0.032741 | 0.093007 | 0.11258 | 0.15308 | 0.2527
Total Head | (m) | 81 | 78.0085 | 66.0327 | 50.093 | 46.1126 | 31.1531 | 1.7527
Water Power | (㎾) | 0 | 0.39036 | 0.65011 | 0.83121 | 0.84183 | 0.66318 | 0.047939
Shaft Power | (㎾) | 0.53048 | 0.97356 | 1.0488 | 1.1651 | 1.2624 | 1.2973 | 1.2107
Pump Eff. | (%) | 0 | 40.0964 | 61.9857 | 71.3439 | 66.6871 | 51.1193 | 3.9597
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 1.48 | 1.91 | 1.93 | 2.14 | 2.22 | 2.29 | 2.27
Motor Input | (㎾) | 0.698 | 1.281 | 1.38 | 1.533 | 1.661 | 1.707 | 1.593
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.1 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 57 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 3.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | FRANKLIN | Turbin | 28
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-9_MF4-1533 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-11)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.7 | 60.3 | 90.7 | 109 | 120.5 | 150 | 172
Dis. Head | (m) | 101 | 92 | 85 | 72 | 60 | 52 | 27 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0084586 | 0.032633 | 0.07383 | 0.10663 | 0.13031 | 0.20193 | 0.26551
Total Head | (m) | 102 | 93.0085 | 86.0326 | 73.0738 | 61.1066 | 53.1303 | 28.2019 | 3.2655
Water Power | (㎾) | 0 | 0.46542 | 0.84561 | 1.0803 | 1.0857 | 1.0436 | 0.68954 | 0.091552
Shaft Power | (㎾) | 0.65016 | 1.0382 | 1.4248 | 1.6884 | 1.7131 | 1.7056 | 1.6216 | 1.4847
Pump Eff. | (%) | 0 | 44.8302 | 59.3471 | 63.9873 | 63.3745 | 61.186 | 42.5216 | 6.1663
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 5.17 | 7.33 | 9.87 | 11.59 | 11.73 | 11.68 | 11.03 | 10.18
Motor Input | (㎾) | 0.945 | 1.509 | 2.071 | 2.454 | 2.49 | 2.479 | 2.357 | 2.158
Motor Eff. | (%) | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 70 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 13.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68.8 | Maker | FRANKLIN | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-11_MF4-2012 |  | Customer |  |  |  | 2 |  | 2006.09.07
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-11)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.4 | 60.4 | 90.6 | 109 | 120 | 150 | 172
Dis. Head | (m) | 100 | 92 | 84 | 72 | 60 | 52 | 27 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.008294 | 0.032741 | 0.073667 | 0.10663 | 0.12924 | 0.20193 | 0.26551
Total Head | (m) | 101 | 93.0083 | 85.0327 | 73.0737 | 61.1066 | 53.1292 | 28.2019 | 3.2655
Water Power | (㎾) | 0 | 0.46087 | 0.83716 | 1.0791 | 1.0857 | 1.0392 | 0.68954 | 0.091552
Shaft Power | (㎾) | 0.59851 | 0.97056 | 1.3163 | 1.5226 | 1.5435 | 1.5394 | 1.4666 | 1.3682
Pump Eff. | (%) | 0 | 47.4854 | 63.5988 | 70.8762 | 70.3408 | 67.5066 | 47.0153 | 6.6913
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.77 | 3.18 | 3.77 | 4.13 | 4.18 | 4.17 | 4.05 | 3.86
Motor Input | (㎾) | 0.888 | 1.44 | 1.953 | 2.259 | 2.29 | 2.284 | 2.176 | 2.03
Motor Eff. | (%) | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 70 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 67.4 | Maker | FRANKLIN | Turbin | 43 | 28
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-11_MF4-2033 |  | Customer |  |  |  | 2 |  | 06/09/05
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-15)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.1 | 60.2 | 90.8 | 114.1 | 120.8 | 150.2 | 175.6
Dis. Head | (m) | 138 | 126.5 | 115 | 99 | 80 | 73 | 40 | 1.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0081312 | 0.032525 | 0.073993 | 0.11684 | 0.13096 | 0.20247 | 0.27674
Total Head | (m) | 139 | 127.5081 | 116.0325 | 100.074 | 81.1168 | 74.131 | 41.2025 | 2.7767
Water Power | (㎾) | 0 | 0.62559 | 1.1386 | 1.4811 | 1.5086 | 1.4597 | 1.0087 | 0.079478
Shaft Power | (㎾) | 0.903 | 1.4014 | 1.9033 | 2.2204 | 2.2666 | 2.2631 | 2.1721 | 2.0216
Pump Eff. | (%) | 0 | 44.6406 | 59.8214 | 66.7058 | 66.5594 | 64.4986 | 46.4409 | 3.9314
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.98 | 9.69 | 12.83 | 14.86 | 15.1 | 15.08 | 14.45 | 13.5
Motor Input | (㎾) | 1.29 | 2.002 | 2.719 | 3.172 | 3.238 | 3.233 | 3.103 | 2.888
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 100 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 17.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | FRANKLIN | Turbin | 47 | 26
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-15_MF4-3012 |  | Customer |  |  |  | 2 |  | 2006.09.11
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-15)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 90.4 | 110.6 | 120.3 | 150.2 | 173
Dis. Head | (m) | 137 | 125 | 114 | 97 | 80 | 71 | 37 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0080772 | 0.032309 | 0.073343 | 0.10978 | 0.12988 | 0.20247 | 0.2686
Total Head | (m) | 138 | 126.0081 | 115.0323 | 98.0733 | 81.1098 | 72.1299 | 38.2025 | 3.2686
Water Power | (㎾) | 0 | 0.61618 | 1.125 | 1.4451 | 1.4622 | 1.4144 | 0.9353 | 0.092171
Shaft Power | (㎾) | 0.87254 | 1.4084 | 1.9061 | 2.2041 | 2.2399 | 2.2304 | 2.1492 | 1.9508
Pump Eff. | (%) | 0 | 43.7513 | 59.021 | 65.567 | 65.2805 | 63.414 | 43.5193 | 4.7248
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.67 | 4.28 | 5.03 | 5.54 | 5.59 | 5.58 | 5.43 | 5.09
Motor Input | (㎾) | 1.192 | 1.924 | 2.604 | 3.011 | 3.06 | 3.047 | 2.936 | 2.665
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 100 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin | 58 | 43
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-15_MF4-3033 |  | Customer |  |  |  | 2 |  | 06/09/04
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-26)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 90 | 109.8 | 120.4 | 150.3 | 175.5
Dis. Head | (m) | 238 | 217 | 197 | 168 | 140 | 122 | 67 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0080772 | 0.032309 | 0.072695 | 0.1082 | 0.1301 | 0.20274 | 0.27642
Total Head | (m) | 239 | 218.0081 | 198.0323 | 169.0727 | 141.1082 | 123.1301 | 68.2027 | 3.2764
Water Power | (㎾) | 0 | 1.0661 | 1.9368 | 2.4803 | 2.5255 | 2.4165 | 1.6709 | 0.093727
Shaft Power | (㎾) | 1.5911 | 2.57 | 3.4593 | 3.9712 | 4.0044 | 3.9928 | 3.7882 | 3.5358
Pump Eff. | (%) | 0 | 41.4811 | 55.9864 | 62.4576 | 63.0679 | 60.5205 | 44.1078 | 2.6508
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 6.13 | 7.2 | 8.47 | 9.32 | 9.36 | 9.36 | 9 | 8.6
Motor Input | (㎾) | 2.061 | 3.329 | 4.481 | 5.144 | 5.187 | 5.172 | 4.907 | 4.58
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 170 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin | 58 | 43
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-26_MF4-5033 |  | Customer |  |  |  | 2 |  | 06/09/14
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(5-39)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60.7 | 90.7 | 113.5 | 120.2 | 150 | 174.7
Dis. Head | (m) | 356 | 325 | 295 | 251 | 200 | 185 | 100 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0080772 | 0.033067 | 0.07383 | 0.11561 | 0.12967 | 0.20193 | 0.27391
Total Head | (m) | 357 | 326.0081 | 296.0331 | 252.0738 | 201.1156 | 186.1297 | 101.2019 | 2.2739
Water Power | (㎾) | 0 | 1.5942 | 2.929 | 3.7267 | 3.7207 | 3.6468 | 2.4744 | 0.064752
Shaft Power | (㎾) | 2.2207 | 3.5601 | 4.8722 | 5.5056 | 5.5315 | 5.5189 | 5.3132 | 4.9439
Pump Eff. | (%) | 0 | 44.7786 | 60.1167 | 67.689 | 67.2646 | 66.0775 | 46.5706 | 1.3097
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 8.35 | 10.04 | 12.19 | 13.38 | 13.41 | 13.35 | 12.92 | 12.26
Motor Input | (㎾) | 3.001 | 4.811 | 6.584 | 7.44 | 7.475 | 7.458 | 7.18 | 6.681
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 80 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 260 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 16 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin | 66 | 26
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-5-39_MF4-7533 |  | Customer |  |  |  | 2 |  | 06/09/14
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification