## Datasheet(60-1-B)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-1-B_MF4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 8 | m | Discharge Piece | STS304
10 | Rated Capacity | 900 | ℓ/min | Impeller | STS304
11 | Shut off Head | 16 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 55 | % | Pump Shaft | STS431
14 | Min. Flow | 400 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1100 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 6.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 383 | mm | Pump | 6.9 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 883 | mm | Total | 23.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-1)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-1_MF4-5033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 10 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 18 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1300 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS410
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 1 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 383 | mm | Pump | 6.9 | kg
37 | Motor | 600 | mm | Motor | 25 | kg
38 | Total | 983 | mm | Total | 31.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-2-BB)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-2-BB_MF4-5033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 13 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 26 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1300 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS410
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 496 | mm | Pump | 9.2 | kg
37 | Motor | 600 | mm | Motor | 25 | kg
38 | Total | 1096 | mm | Total | 34.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-2)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-2_MF4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 20 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 38 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1300 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 16 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 2 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 496 | mm | Pump | 9.2 | kg
37 | Motor | 752 | mm | Motor | 31.8 | kg
38 | Total | 1248 | mm | Total | 41 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-3-A)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-3-A_MF6-10033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 35 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 53 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 7.5 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 19.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 3 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 609 | mm | Pump | 11.5 | kg
37 | Motor | 645 | mm | Motor | 52 | kg
38 | Total | 1254 | mm | Total | 63.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-4)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-4_MF6-15033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 48 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 77 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 11 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 28.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 722 | mm | Pump | 13.7 | kg
37 | Motor | 711 | mm | Motor | 58 | kg
38 | Total | 1433 | mm | Total | 71.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-6-B)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-6-B_MF6-20033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 70 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 105 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 15 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 37.3 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 948 | mm | Pump | 18.3 | kg
37 | Motor | 777 | mm | Motor | 64 | kg
38 | Total | 1725 | mm | Total | 82.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-7)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-7_MF6-25033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 80 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 135 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 19 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 45.4 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1061 | mm | Pump | 20.6 | kg
37 | Motor | 841 | mm | Motor | 70 | kg
38 | Total | 1902 | mm | Total | 90.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-9-B)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-9-B_MF6-30033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 110 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 165 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 22 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 55.4 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 9 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1287 | mm | Pump | 25.1 | kg
37 | Motor | 907 | mm | Motor | 76 | kg
38 | Total | 2194 | mm | Total | 101.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-11)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-11_MF6-40033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 120 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 225 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 550 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 30 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 75 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 11 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1513 | mm | Pump | 29.7 | kg
37 | Motor | 1036 | mm | Motor | 92 | kg
38 | Total | 2549 | mm | Total | 121.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(60-14)
Submersible Motor Pump Data Sheet
1 | Model | PSS-60-14_MF6-50033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 170 | m | Discharge Piece | STS304
10 | Rated Capacity | 1000 | ℓ/min | Impeller | STS304
11 | Shut off Head | 270 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 70 | % | Pump Shaft | STS431
14 | Min. Flow | 600 | ℓ/min | Coupling | STS304
15 | Max. Flow | 1400 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 100 | mm | Strainer | STS304
17 | Out Dia. | 145mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 37 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 94.5 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 138 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 1580 kgf / 3500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 14 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1852 | mm | Pump | 36.5 | kg
37 | Motor | 1405 | mm | Motor | 136 | kg
38 | Total | 3257 | mm | Total | 172.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-60-1-B | MF4-3012 | 383 |  |  | 560 |  |  | 943
| MF4-3033 |  |  |  | 500 |  |  | 883
PSS-60-1 | MF4-5033 | 383 |  |  | 600 |  |  | 983
PSS-60-2-BB | MF4-5033 | 496 |  |  | 600 |  |  | 1096
PSS-60-2 | MF4-7533 | 496 |  |  | 752 |  |  | 1248
PSS-60-3-A | MF6-10033 | 609 |  |  | 645 |  |  | 1254
PSS-60-4 | MF6-15033 | 722 |  |  | 711 |  |  | 1433
PSS-60-6-B | MF6-20033 | 948 |  |  | 777 |  |  | 1725
PSS-60-6 | MF6-25033 | 948 |  |  | 841 |  |  | 1789
PSS-60-7 | MF6-25033 | 1061 |  |  | 841 |  |  | 1902
PSS-60-8 | MF6-30033 | 1174 |  |  | 907 |  |  | 2081
PSS-60-9-B | MF6-30033 | 1287 |  |  | 907 |  |  | 2194
PSS-60-11 | MF6-40033 | 1513 |  |  | 1036 |  |  | 2549
PSS-60-12 | MF6-50033 | 1626 |  |  | 1405 |  |  | 3031
PSS-60-13 | MF6-50033 | 1739 |  |  | 1405 |  |  | 3144
PSS-60-14 | MF6-50033 | 1852 |  |  | 1405 |  |  | 3257
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-60-1-B | MF4-3012 | 6.9 |  |  | 20 |  |  | 26.9
| MF4-3033 |  |  |  | 17 |  |  | 23.9
PSS-60-1 | MF4-5033 | 6.9 |  |  | 25 |  |  | 31.9
PSS-60-2-BB | MF4-5033 | 9.2 |  |  | 25 |  |  | 34.2
PSS-60-2 | MF4-7533 | 9.2 |  |  | 31.8 |  |  | 41
PSS-60-3-A | MF6-10033 | 11.5 |  |  | 52 |  |  | 63.5
PSS-60-4 | MF6-15033 | 13.7 |  |  | 58 |  |  | 71.7
PSS-60-6-B | MF6-20033 | 18.3 |  |  | 64 |  |  | 82.3
PSS-60-6 | MF6-25033 | 18.3 |  |  | 70 |  |  | 88.3
PSS-60-7 | MF6-25033 | 20.6 |  |  | 70 |  |  | 90.6
PSS-60-8 | MF6-30033 | 22.9 |  |  | 76 |  |  | 98.9
PSS-60-9-B | MF6-30033 | 25.1 |  |  | 76 |  |  | 101.1
PSS-60-11 | MF6-40033 | 29.7 |  |  | 92 |  |  | 121.7
PSS-60-12 | MF6-50033 | 32 |  |  | 136 |  |  | 168
PSS-60-13 | MF6-50033 | 34.3 |  |  | 136 |  |  | 170.3
PSS-60-14 | MF6-50033 | 36.5 |  |  | 136 |  |  | 172.5
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 4" (100mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
145mm
P.L
M.L
T.L
Cable Guard Included
Outline Drawing
of PSS-60 Series

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | 품 명 |  |  | 재 질 |  | 수량
1 | Discharge |  |  | STS304 |  | 1
2 | Valve Cone |  |  |  |  | 1
3 | Valve Seat |  |  | NBR |  | Stages
4 | Top Diffuser |  |  | STS304 |  | 1
5 | Upper Bearing |  |  |  |  | 1
6 | Neck Ring |  |  | NBR |  | 1
7 | Bearing |  |  |  |  | 1
8 | Diffuser |  |  | STS304 |  | Stages
9 | Split Cone Nut |  |  |  |  | Stages
10 | Split Cone |  |  |  |  | Stages
11 | Impeller Ring |  |  |  |  | Stages
12 | Impeller |  |  |  |  | Stages
13 | Buttom Diffuser |  |  |  |  | 1
14 | Lower Bearing |  |  | - |  | 1
15 | Stop Ring |  |  | - |  | 1
16 | Space Washer |  |  | STS304 |  | 1
17 | Nut for Stop Ring |  |  |  |  | 1
18 | Buttom Neck Ring |  |  | NBR |  | 1
19 | Strainer |  |  | STS304 |  | 1
20 | Suction Interconnector |  |  |  |  | 1
21 | Pump Shaft |  |  | STS431 |  | 1
22 | Coupling |  |  | STS304 |  | 1
23 | Strap |  |  |  |  | 4
24 | Nut |  |  |  |  | 4
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-60 Series

## Test Report(60-1-B)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 200 | 400 | 600 | 853 | 1105 | 1418
Dis. Head | (m) | 14.9 | 14 | 12.6 | 10.7 | 8 | 6 | 0.2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.03676 | 0.082711 | 0.16717 | 0.28053 | 0.46197
Total Head | (m) | 15.9 | 15.0092 | 13.6368 | 11.7827 | 9.1672 | 7.2805 | 1.662
Water Power | (㎾) | 0 | 0.4893 | 0.88912 | 1.1523 | 1.2746 | 1.3113 | 0.38414
Shaft Power | (㎾) | 1.5204 | 1.6946 | 1.7993 | 1.92 | 2.0372 | 2.166 | 2.1565
Pump Eff. | (%) | 0 | 28.8744 | 49.4158 | 60.0171 | 62.5673 | 60.542 | 17.8132
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.64 | 4.91 | 5.08 | 5.23 | 5.42 | 5.61 | 5.61
Motor Input | (㎾) | 2.077 | 2.315 | 2.458 | 2.623 | 2.783 | 2.959 | 2.946
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 900 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 8 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-1-B_MF-3033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-1)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 300 | 603 | 905 | 1203 | 1532
Dis. Head | (m) | 19 | 17.8 | 14.2 | 9 | 6 | 0.1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020678 | 0.08354 | 0.18817 | 0.3325 | 0.53923
Total Head | (m) | 21.2 | 20.0207 | 16.4835 | 11.3882 | 8.5325 | 2.8392
Water Power | (㎾) | 0 | 0.97901 | 1.6202 | 1.6799 | 1.6731 | 0.709
Shaft Power | (㎾) | 2.7252 | 3.0185 | 3.0417 | 3.1112 | 3.3659 | 3.4508
Pump Eff. | (%) | 0 | 32.4335 | 53.265 | 53.9968 | 49.7079 | 20.5458
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.6 | 8.05 | 8.1 | 8.21 | 8.58 | 8.7
Motor Input | (㎾) | 3.53 | 3.91 | 3.94 | 4.03 | 4.36 | 4.47
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 10 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.2
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-1_MF4-5033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-2-BB)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 202 | 401 | 602 | 856 | 1060 | 1480
Dis. Head | (m) | 27.5 | 26.8 | 24.2 | 21 | 16.8 | 12.5 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0093748 | 0.036944 | 0.083263 | 0.16835 | 0.25815 | 0.50325
Total Head | (m) | 28.5 | 27.8094 | 25.2369 | 22.0833 | 17.9683 | 13.7581 | 2.5032
Water Power | (㎾) | 0 | 0.91565 | 1.6496 | 2.1669 | 2.5071 | 2.3771 | 0.60388
Shaft Power | (㎾) | 3.9449 | 3.3968 | 3.5126 | 3.7288 | 3.8986 | 3.9604 | 3.5358
Pump Eff. | (%) | 0 | 26.9563 | 46.9613 | 58.1143 | 64.3074 | 60.0232 | 17.0793
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 8.09 | 8.61 | 8.8 | 9.14 | 9.41 | 9.49 | 8.86
Motor Input | (㎾) | 5.11 | 4.4 | 4.55 | 4.83 | 5.05 | 5.13 | 4.58
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 13 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-2-BB_MF4-5033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-2)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 359 | 656 | 962 | 1257 | 1644
Dis. Head | (m) | 39 | 36 | 29 | 21 | 15 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.029611 | 0.098871 | 0.21262 | 0.36302 | 0.62096
Total Head | (m) | 41.5 | 38.5296 | 31.5989 | 23.7126 | 17.863 | 3.121
Water Power | (㎾) | 0 | 2.2546 | 3.3788 | 3.7183 | 3.66 | 0.83633
Shaft Power | (㎾) | 4.6102 | 5.18 | 5.2614 | 5.4316 | 5.6684 | 5.4094
Pump Eff. | (%) | 0 | 43.5258 | 64.2187 | 68.4565 | 64.568 | 15.4607
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 12.13 | 13.08 | 13.21 | 13.55 | 13.98 | 13.47
Motor Input | (㎾) | 6.23 | 7 | 7.11 | 7.34 | 7.66 | 7.31
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 20 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 16 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | Franklin | Turbin | 15
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-2_MF4-7533 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-3-A)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 308 | 606 | 911 | 1285 | 1408 | 1692
Dis. Head | (m) | 54.5 | 52 | 44.5 | 36 | 25 | 17 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.021795 | 0.084373 | 0.19068 | 0.37937 | 0.45547 | 0.65775
Total Head | (m) | 57 | 54.5218 | 47.0844 | 38.6907 | 27.8794 | 19.9555 | 3.1577
Water Power | (㎾) | 0 | 2.7372 | 4.6509 | 5.7453 | 5.8395 | 4.5799 | 0.87089
Shaft Power | (㎾) | 6.8468 | 7.8468 | 8.0886 | 8.2446 | 8.4786 | 8.4006 | 7.6752
Pump Eff. | (%) | 0 | 34.8832 | 57.4994 | 69.6855 | 68.8731 | 54.5183 | 11.3469
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 15.56 | 17.37 | 17.83 | 18.12 | 18.64 | 18.45 | 17.06
Motor Input | (㎾) | 8.778 | 10.06 | 10.37 | 10.57 | 10.87 | 10.77 | 9.84
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 7.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 35 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 19.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | FRANKLIN | Turbin | 12
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-3-A_MF6-10033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-4)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 308 | 616 | 900 | 1232 | 1504 | 1742
Dis. Head | (m) | 79 | 78 | 65 | 50 | 38 | 21 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.021795 | 0.087181 | 0.1861 | 0.34872 | 0.5197 | 0.6972
Total Head | (m) | 81.5 | 80.5218 | 67.5872 | 52.6861 | 40.8487 | 24.0197 | 3.1972
Water Power | (㎾) | 0 | 4.0425 | 6.7863 | 7.7291 | 8.2031 | 5.8885 | 0.90783
Shaft Power | (㎾) | 9.3353 | 10.819 | 11.1799 | 11.4526 | 11.7493 | 11.3884 | 10.3378
Pump Eff. | (%) | 0 | 37.365 | 60.701 | 67.4875 | 69.8176 | 51.7059 | 8.7817
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 23.03 | 25.54 | 26.18 | 26.73 | 27.19 | 26.53 | 24.65
Motor Input | (㎾) | 11.64 | 13.49 | 13.94 | 14.28 | 14.65 | 14.2 | 12.89
Motor Eff. | (%) | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2 | 80.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 11 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 48 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 28.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 80.2 | Maker | Franklin | Turbin | 16
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-4_MF6-15033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-6-B)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 360 | 615 | 1044 | 1220 | 1510 | 1754
Dis. Head | (m) | 110 | 102 | 93 | 75 | 60 | 38 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.029776 | 0.086898 | 0.25041 | 0.34196 | 0.52386 | 0.70684
Total Head | (m) | 112.5 | 104.5298 | 95.5869 | 77.7504 | 62.842 | 41.0239 | 3.2068
Water Power | (㎾) | 0 | 6.1338 | 9.5821 | 13.2309 | 12.4968 | 10.0972 | 0.91684
Shaft Power | (㎾) | 11.579 | 13.921 | 15.5856 | 17.4706 | 17.3074 | 16.3934 | 14.892
Pump Eff. | (%) | 0 | 44.0617 | 61.4805 | 75.7328 | 72.2048 | 61.5929 | 6.1566
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 27.56 | 31.57 | 34.49 | 37.96 | 37.61 | 35.94 | 33.17
Motor Input | (㎾) | 14.19 | 17.06 | 19.1 | 21.41 | 21.21 | 20.09 | 18.25
Motor Eff. | (%) | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 15 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 70 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 37.3 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 81.6 | Maker | Franklin | Turbin | 16 | 16
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-6-B_MF6-20033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-7)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 360 | 615 | 1044 | 1220 | 1510 | 1754
Dis. Head | (m) | 138 | 135 | 117 | 83 | 69 | 40 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.029776 | 0.086898 | 0.25041 | 0.34196 | 0.52386 | 0.70684
Total Head | (m) | 140.5 | 137.5298 | 119.5869 | 85.7504 | 71.842 | 43.0239 | 3.2068
Water Power | (㎾) | 0 | 8.0702 | 11.988 | 14.5923 | 14.2865 | 10.5895 | 0.91684
Shaft Power | (㎾) | 16.3344 | 19.0896 | 19.393 | 19.9096 | 19.7866 | 18.9092 | 16.4656
Pump Eff. | (%) | 0 | 42.2756 | 61.8161 | 73.2929 | 72.2029 | 56.0016 | 5.5682
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 37.73 | 42.67 | 43.15 | 44.05 | 42.8 | 42.17 | 37.7
Motor Input | (㎾) | 19.92 | 23.28 | 23.65 | 24.28 | 24.13 | 23.06 | 20.08
Motor Eff. | (%) | 82 | 82 | 82 | 82 | 82 | 82 | 82
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 21.4 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 80 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 45.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82 | Maker | Franklin | Turbin | 15.5
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-7_MF6-25033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Suc. Head | m | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Vacuum | mmhg | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432 | 441.432
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-9-B)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 522 | 1005 | 1257 | 1509 | 1768
Dis. Head | (m) | 170 | 160 | 112 | 87 | 55 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.15284 | 0.56654 | 0.88628 | 1.2773 | 1.7533
Total Head | (m) | 172.5 | 162.6528 | 115.0665 | 90.3863 | 58.7773 | 5.2533
Water Power | (㎾) | 0 | 13.8395 | 18.8496 | 18.5193 | 14.4573 | 1.5139
Shaft Power | (㎾) | 22.302 | 26.1016 | 26.5146 | 26.3494 | 25.0278 | 21.9716
Pump Eff. | (%) | 0 | 53.0216 | 71.0915 | 70.2837 | 57.7648 | 6.8904
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 47 | 54 | 55 | 54 | 53 | 46
Motor Input | (㎾) | 27 | 31.6 | 32.1 | 31.9 | 30.3 | 26.6
Motor Eff. | (%) | 82.6 | 82.6 | 82.6 | 82.6 | 82.6 | 82.6
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 22 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 110 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 80 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 55.4 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82.6 | Maker | FRANKLIN | Turbin | 14 | 14
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-9-B_MF6-30033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-11)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 478 | 688 | 890 | 1100 | 1325 | 1640
Dis. Head | (m) | 227 | 200 | 170 | 150 | 120 | 80 | 10
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.052495 | 0.10875 | 0.18199 | 0.278 | 0.40336 | 0.61794
Total Head | (m) | 228.5 | 201.5525 | 171.6088 | 151.682 | 121.778 | 81.9034 | 12.1179
Water Power | (㎾) | 0 | 15.7038 | 19.2449 | 22.0045 | 21.8348 | 17.6891 | 3.2394
Shaft Power | (㎾) | 25.4196 | 30.222 | 30.4704 | 30.636 | 30.8016 | 29.5596 | 24.6744
Pump Eff. | (%) | 0 | 51.9614 | 63.1593 | 71.8256 | 70.8885 | 59.8421 | 13.1285
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 58.5 | 66.5 | 66.8 | 67.1 | 67.4 | 65.1 | 56.9
Motor Input | (㎾) | 30.7 | 36.5 | 36.8 | 37 | 37.2 | 35.7 | 29.8
Motor Eff. | (%) | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 30 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 120 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 1.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 75 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 82.8 | Maker | FRANKLIN | Turbin | 19.5 | 19.5
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-11_MF6-40033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(60-14)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 412 | 823 | 1211 | 1516 | 1785
Dis. Head | (m) | 275 | 264 | 201 | 148 | 87 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.038999 | 0.15562 | 0.33694 | 0.52803 | 0.73204
Total Head | (m) | 277.5 | 266.539 | 203.6556 | 150.8369 | 90.028 | 3.232
Water Power | (㎾) | 0 | 17.8997 | 27.3202 | 29.7742 | 22.2466 | 0.94038
Shaft Power | (㎾) | 32.7031 | 39.0878 | 40.3218 | 40.7332 | 38.685 | 32.2489
Pump Eff. | (%) | 0 | 45.7936 | 67.7553 | 73.0955 | 57.5072 | 2.916
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 69.64 | 80.97 | 83.09 | 84.27 | 80.2 | 68.72
Motor Input | (㎾) | 38.16 | 45.61 | 47.05 | 47.53 | 45.14 | 37.63
Motor Eff. | (%) | 85.7 | 85.7 | 85.7 | 85.7 | 85.7 | 85.7
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 1000 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 37 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 170 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 100 | 2.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 94.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 85.7 | Maker | FRANKLIN | Turbin | 23 | 23
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-60-14_MF6-50033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification