## Datasheet(8-4)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-8-4_MF4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 25 | m | Discharge Piece | STS304
10 | Rated Capacity | 130 | ℓ/min | Impeller | STS304
11 | Shut off Head | 32 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 70 | ℓ/min | Coupling | STS304
15 | Max. Flow | 200 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 9.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 370 | mm | Pump | 3.8 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 668 | mm | Total | 14.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(8-4)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-8-4_MF4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 25 | m | Discharge Piece | STS304
10 | Rated Capacity | 130 | ℓ/min | Impeller | STS304
11 | Shut off Head | 32 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 70 | ℓ/min | Coupling | STS304
15 | Max. Flow | 200 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kW | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 2.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 4 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 370 | mm | Pump | 3.8 | kg
37 | Motor | 298 | mm | Motor | 10.9 | kg
38 | Total | 668 | mm | Total | 14.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(8-5)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-8-5_MF4-1512 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 34 | m | Discharge Piece | STS304
10 | Rated Capacity | 130 | ℓ/min | Impeller | STS304
11 | Shut off Head | 40 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 70 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.1 | kW | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 11.5 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 412 | mm | Pump | 4.3 | kg
37 | Motor | 345 | mm | Motor | 12.6 | kg
38 | Total | 757 | mm | Total | 16.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(8-5)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-8-5_MF4-1533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 34 | m | Discharge Piece | STS304
10 | Rated Capacity | 130 | ℓ/min | Impeller | STS304
11 | Shut off Head | 40 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 70 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.1 | kw | Stud | STS302
22 | Power Supply | 3phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 3.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 412 | mm | Pump | 4.3 | kg
37 | Motor | 298 | mm | Motor | 11.5 | kg
38 | Total | 710 | mm | Total | 15.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(8-7)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-8-7_MF4-2012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 44 | m | Discharge Piece | STS304
10 | Rated Capacity | 130 | ℓ/min | Impeller | STS304
11 | Shut off Head | 55 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 70 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 13.2 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 496 | mm | Pump | 5.3 | kg
37 | Motor | 384 | mm | Motor | 14.5 | kg
38 | Total | 880 | mm | Total | 19.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(8-7)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-8-7_MF4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 44 | m | Discharge Piece | STS304
10 | Rated Capacity | 130 | ℓ/min | Impeller | STS304
11 | Shut off Head | 55 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 70 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 4.9 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 300 kgf / 650 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 496 | mm | Pump | 5.3 | kg
37 | Motor | 346 | mm | Motor | 13.1 | kg
38 | Total | 842 | mm | Total | 18.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(8-9)1P
Submersible Motor Pump Data Sheet
1 | Model | PSS-8-9_MF4-3012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 58 | m | Discharge Piece | STS304
10 | Rated Capacity | 130 | ℓ/min | Impeller | STS304
11 | Shut off Head | 72 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 70 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 17 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 9 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 580 | mm | Pump | 6.3 | kg
37 | Motor | 560 | mm | Motor | 20 | kg
38 | Total | 1140 | mm | Total | 26.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(8-9)3P
Submersible Motor Pump Data Sheet
1 | Model | PSS-8-9_MF4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 58 | m | Discharge Piece | STS304
10 | Rated Capacity | 130 | ℓ/min | Impeller | STS304
11 | Shut off Head | 72 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 70 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 6.6 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.3 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 415 kgf / 900 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 9 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 580 | mm | Pump | 6.3 | kg
37 | Motor | 500 | mm | Motor | 17 | kg
38 | Total | 1080 | mm | Total | 23.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(8-15)
Submersible Motor Pump Data Sheet
1 | Model | PSS-8-15_MF4-5033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 95 | m | Discharge Piece | STS304
10 | Rated Capacity | 130 | ℓ/min | Impeller | STS304
11 | Shut off Head | 120 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 55 | % | Pump Shaft | STS431
14 | Min. Flow | 70 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS410
21 | Rated Power | 3.7 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 10.8 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 15 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 832 | mm | Pump | 9.3 | kg
37 | Motor | 600 | mm | Motor | 25 | kg
38 | Total | 1432 | mm | Total | 34.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(8-25)
Submersible Motor Pump Data Sheet
1 | Model | PSS-8-25_MF4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 160 | m | Discharge Piece | STS304
10 | Rated Capacity | 130 | ℓ/min | Impeller | STS304
11 | Shut off Head | 205 | m | Diffuser | STS304
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 60 | % | Pump Shaft | STS431
14 | Min. Flow | 70 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Straps | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | Franklin Electric USA |  | Stator Shell | STS301
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | STS302
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | Acetal
23 | Pole | 2 | p | Seal | NR
24 | Max. Load Current | 16 | A | Diaphragm | NR
25 | Insulation Class | F | class | Diaphragm Cover | STS301
26 | Operating Cond. | Continuous |  | Slinger | NR
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95.25 | mm | Lead Jam Nut | STS303
29 | Max. downthrust | 680 kgf / 1500 lbs |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 25 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1252 | mm | Pump | 14.3 | kg
37 | Motor | 752 | mm | Motor | 31.8 | kg
38 | Total | 2004 | mm | Total | 46.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PSS-8-4 | MF4-1012 | 4 |  |  | 1 |  | 1 | 220 | 60
| MF4-1033 | [5 empty] | 3 | 380
PSS-8-5 | MF4-1512 | 5 |  |  | 1.5 |  | 1 | 220
| MF4-1533 | [5 empty] | 3 | 380
PSS-8-7 | MF4-2012 | 7 |  |  | 2 |  | 1 | 220
| MF4-2033 | [5 empty] | 3 | 380
PSS-8-9 | MF4-3012 | 9 |  |  | 3 |  | 1 | 220
| MF4-3033 | [5 empty] | 3 | 380
PSS-8-12 | MF4-5033 | 12 |  |  | 5 |  | 3 | 380
PSS-8-15 | MF4-5033 | 15 |  |  | 5 |  | 3 | 380
PSS-8-21 | MF4-7533 | 21 |  |  | 7.5 |  | 3 | 380
PSS-8-25 | MF4-7533 | 25 |  |  | 7.5 |  | 3 | 380
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PSS-8-4 | MF4-1012 | 370 |  |  | 298 |  |  | 668
| MF4-1033 | 370 |  |  | 298 |  |  | 668
PSS-8-5 | MF4-1512 | 412 |  |  | 345 |  |  | 757
| MF4-1533 | 412 |  |  | 298 |  |  | 710
PSS-8-7 | MF4-2012 | 496 |  |  | 384 |  |  | 880
| MF4-2033 | 496 |  |  | 346 |  |  | 842
PSS-8-9 | MF4-3012 | 580 |  |  | 560 |  |  | 1140
| MF4-3033 | 580 |  |  | 500 |  |  | 1080
PSS-8-12 | MF4-5033 | 706 |  |  | 600 |  |  | 1306
PSS-8-15 | MF4-5033 | 832 |  |  | 600 |  |  | 1432
PSS-8-21 | MF4-7533 | 1084 |  |  | 752 |  |  | 1836
PSS-8-25 | MF4-7533 | 1252 |  |  | 752 |  |  | 2004
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PSS-8-4 | MF4-1012 | 3.8 |  |  | 10.9 |  |  | 14.7
| MF4-1033 |  |  |  | 10.9 |  |  | 14.7
PSS-8-5 | MF4-1512 | 4.3 |  |  | 12.6 |  |  | 16.9
| MF4-1533 |  |  |  | 11.5 |  |  | 15.8
PSS-8-7 | MF4-2012 | 5.3 |  |  | 14.5 |  |  | 19.8
| MF4-2033 |  |  |  | 13.1 |  |  | 18.4
PSS-8-9 | MF4-3012 | 6.3 |  |  | 20 |  |  | 26.3
| MF4-3033 |  |  |  | 17 |  |  | 23.3
PSS-8-12 | MF4-5033 | 7.8 |  |  | 25 |  |  | 32.8
PSS-8-15 | MF4-5033 | 9.3 |  |  | 25 |  |  | 34.3
PSS-8-21 | MF4-7533 | 12.3 |  |  | 31.8 |  |  | 44.1
PSS-8-25 | MF4-7533 | 14.3 |  |  | 31.8 |  |  | 46.1
※MOTOR MAKER : FRANKLIN ELECTRIC U.S.A
※DISCHARGE CONNECTION : 2" (50mm)
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PSS-8 Series
98mm
P.L
M.L
T.L
P.L
M.L
T.L
Cable Guard Included

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge piece |  |  | STS304 |  | 1
2 | Valve cone |  |  |  |  | 1
3 | Valve seat |  |  | NBR |  | 1
4 | Bearing |  |  | NBR |  | 1
5 | Top intermediate chamber |  |  | - |  | 1
6 | Split cone nut |  |  | NBR |  | Stages
7 | Impeller |  |  |  |  | Stages
8 | Split cone |  |  | STS304 |  | Stages
9 | Neck ring |  |  | NBR |  | Stages
10 | Diffuser |  |  | STS304 |  | Stages
11 | Bottom diffuser |  |  |  |  | 1
12 | Strainer |  |  |  |  | 1
13 | Suction interconnector |  |  |  |  | 1
14 | Pump shaft/coupling |  |  | STS431/304 |  | 1
15 | Strap |  |  | STS304 |  | 4
16 | Nut |  |  |  |  | 4
17 | Cable guard |  |  |  |  | 1
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PSS-8 Series

## Test Report(8-4)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 100 | 167 | 200 | 250 | 268
Dis. Head | (m) | 33 | 30 | 27 | 22 | 15.8 | 5.6 | 1.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.03676 | 0.10252 | 0.14704 | 0.22975 | 0.26403
Total Head | (m) | 34 | 31.0092 | 28.0368 | 23.1025 | 16.947 | 6.8298 | 2.764
Water Power | (㎾) | 0 | 0.25272 | 0.457 | 0.62887 | 0.55247 | 0.27831 | 0.12074
Shaft Power | (㎾) | 0.42189 | 0.60327 | 0.76572 | 0.9161 | 0.88568 | 0.79499 | 0.76514
Pump Eff. | (%) | 0 | 41.8922 | 59.6826 | 68.6465 | 62.3783 | 35.0083 | 15.7806
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.65 | 7.3 | 8.12 | 9.05 | 8.85 | 8.29 | 8.12
Motor Input | (㎾) | 0.735 | 1.051 | 1.334 | 1.596 | 1.543 | 1.385 | 1.333
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 25 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 9.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | FRANKLIN | Turbin | 26 | 25
Item No. |  |  | Serial No. | 50500021 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-8-4_MF4-1012 |  | Customer |  |  |  | 2 |  | 05/04/10
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(8-4)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 100 | 167 | 200 | 250 | 268
Dis. Head | (m) | 33 | 30 | 27 | 22 | 15.8 | 5.6 | 1.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.03676 | 0.10252 | 0.14704 | 0.22975 | 0.26403
Total Head | (m) | 34 | 31.0092 | 28.0368 | 23.1025 | 16.947 | 6.8298 | 2.764
Water Power | (㎾) | 0 | 0.25272 | 0.457 | 0.62887 | 0.55247 | 0.27831 | 0.12074
Shaft Power | (㎾) | 0.3241 | 0.8946 | 1.0192 | 1.0542 | 1.0591 | 1.0451 | 0.7336
Pump Eff. | (%) | 0 | 28.25 | 44.839 | 59.6541 | 52.1644 | 26.6302 | 16.4591
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.85 | 1.96 | 2.08 | 2.23 | 2.23 | 2.21 | 2.18
Motor Input | (㎾) | 0.463 | 1.278 | 1.456 | 1.506 | 1.513 | 1.493 | 1.048
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 25 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 2.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | FRANKLIN | Turbin | 26 | 25
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-8-4_MF4-1033 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(8-5)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 100 | 167 | 200 | 250 | 268
Dis. Head | (m) | 40 | 37 | 37 | 30 | 20 | 7 | 1.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.03676 | 0.10252 | 0.14704 | 0.22975 | 0.26403
Total Head | (m) | 41 | 38.0092 | 38.0368 | 31.1025 | 21.147 | 8.2298 | 2.764
Water Power | (㎾) | 0 | 0.30977 | 0.62 | 0.84664 | 0.68939 | 0.33536 | 0.12074
Shaft Power | (㎾) | 0.5586 | 0.79876 | 1.0138 | 1.213 | 1.1727 | 1.0526 | 1.0131
Pump Eff. | (%) | 0 | 38.782 | 61.1536 | 69.7996 | 58.7879 | 31.8604 | 11.9185
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.65 | 7.3 | 8.12 | 9.05 | 8.85 | 8.29 | 8.12
Motor Input | (㎾) | 0.735 | 1.051 | 1.334 | 1.596 | 1.543 | 1.385 | 1.333
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.1 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 34 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 11.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | FRANKLIN | Turbin | 26 | 25
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-8-5_MF4-1512 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(8-5)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 100 | 167 | 200 | 250 | 268
Dis. Head | (m) | 40 | 37 | 37 | 30 | 20 | 7 | 1.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.03676 | 0.10252 | 0.14704 | 0.22975 | 0.26403
Total Head | (m) | 41 | 38.0092 | 38.0368 | 31.1025 | 21.147 | 8.2298 | 2.764
Water Power | (㎾) | 0 | 0.30977 | 0.62 | 0.84664 | 0.68939 | 0.33536 | 0.12074
Shaft Power | (㎾) | 0.35188 | 0.97128 | 1.1066 | 1.1446 | 1.1499 | 1.1347 | 0.79648
Pump Eff. | (%) | 0 | 31.8935 | 56.0294 | 73.9709 | 59.9535 | 29.5557 | 15.1597
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 1.85 | 1.96 | 2.08 | 2.23 | 2.23 | 2.21 | 2.18
Motor Input | (㎾) | 0.463 | 1.278 | 1.456 | 1.506 | 1.513 | 1.493 | 1.048
Motor Eff. | (%) | 76 | 76 | 76 | 76 | 76 | 76 | 76
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.1 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 34 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 3.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 76 | Maker | FRANKLIN | Turbin | 26 | 25
Item No. |  |  | Serial No. |  | Inspector |  | Run (Hr) | B/R (℃) | Test Date
Model | PSS-8-5_MF4-1533 |  | Customer |  |  |  | 2
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(8-7)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50.5 | 100.5 | 150.3 | 166 | 200 | 250 | 279.6
Dis. Head | (m) | 58 | 53 | 48 | 43 | 40 | 31 | 14 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0093748 | 0.037129 | 0.083042 | 0.1013 | 0.14704 | 0.22975 | 0.28738
Total Head | (m) | 59 | 54.0094 | 49.0371 | 44.083 | 41.1013 | 32.147 | 15.2298 | 3.7874
Water Power | (㎾) | 0 | 0.44458 | 0.8033 | 1.08 | 1.1121 | 1.048 | 0.62061 | 0.17261
Shaft Power | (㎾) | 0.6763 | 1.0616 | 1.4242 | 1.7007 | 1.7386 | 1.6787 | 1.4744 | 1.3932
Pump Eff. | (%) | 0 | 41.8788 | 56.4053 | 63.5011 | 63.9672 | 62.4281 | 42.093 | 12.3894
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 5.29 | 7.54 | 9.82 | 11.64 | 11.93 | 11.44 | 10.1 | 9.55
Motor Input | (㎾) | 0.983 | 1.543 | 2.07 | 2.472 | 2.527 | 2.44 | 2.143 | 2.025
Motor Eff. | (%) | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8 | 68.8
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 44 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 13.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68.8 | Maker | FRANKLIN | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-8-7_MF4-2012 |  | Customer |  |  |  | 2 |  | 2006.09.07
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(8-7)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.7 | 80.5 | 120 | 168 | 200 | 240 | 277
Dis. Head | (m) | 58 | 54 | 50 | 46 | 40 | 31 | 17 | 5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0060893 | 0.023822 | 0.052935 | 0.10375 | 0.14704 | 0.21174 | 0.28206
Total Head | (m) | 59 | 55.0061 | 51.0238 | 47.0529 | 41.1038 | 32.147 | 18.2117 | 6.2821
Water Power | (㎾) | 0 | 0.36492 | 0.66951 | 0.92036 | 1.1256 | 1.048 | 0.71244 | 0.28364
Shaft Power | (㎾) | 0.64232 | 0.93686 | 1.1997 | 1.4323 | 1.5812 | 1.5374 | 1.406 | 1.3028
Pump Eff. | (%) | 0 | 38.951 | 55.8054 | 64.2594 | 71.1853 | 68.1669 | 50.6729 | 21.771
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.88 | 3.19 | 3.6 | 3.99 | 4.3 | 4.21 | 3.96 | 3.77
Motor Input | (㎾) | 0.953 | 1.39 | 1.78 | 2.125 | 2.346 | 2.281 | 2.086 | 1.933
Motor Eff. | (%) | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4 | 67.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 44 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 67.4 | Maker | FRANKLIN | Turbin | 43 | 28
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-8-7_MF4-2033 |  | Customer |  |  |  | 2 |  | 06/09/06
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(8-9)1P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 100.8 | 150.1 | 182 | 200.7 | 250 | 283
Dis. Head | (m) | 75 | 70 | 63 | 58 | 50 | 42 | 21 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.037351 | 0.082821 | 0.12176 | 0.14807 | 0.22975 | 0.29441
Total Head | (m) | 76 | 71.0092 | 64.0374 | 59.0828 | 51.1218 | 43.1481 | 22.2298 | 3.2944
Water Power | (㎾) | 0 | 0.57872 | 1.0522 | 1.4455 | 1.5166 | 1.4116 | 0.90586 | 0.15197
Shaft Power | (㎾) | 0.8925 | 1.379 | 1.8326 | 2.1658 | 2.226 | 2.1665 | 1.9306 | 1.82
Pump Eff. | (%) | 0 | 41.967 | 57.4135 | 66.7438 | 68.1302 | 65.1535 | 46.9213 | 8.3499
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.86 | 9.55 | 12.37 | 14.53 | 14.93 | 14.54 | 12.93 | 12.22
Motor Input | (㎾) | 1.275 | 1.97 | 2.618 | 3.094 | 3.18 | 3.095 | 2.758 | 2.6
Motor Eff. | (%) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 58 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 17.0 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 70 | Maker | FRANKLIN | Turbin | 20 | 20
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-8-9_MF4-3012 |  | Customer |  |  |  | 2 |  | 2006.09.12
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(8-9)3P
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50.5 | 100 | 150.8 | 179.8 | 200 | 250 | 281.5
Dis. Head | (m) | 75 | 68 | 62 | 57 | 50 | 41 | 19 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0093748 | 0.03676 | 0.083595 | 0.11884 | 0.14704 | 0.22975 | 0.2913
Total Head | (m) | 76 | 69.0094 | 63.0368 | 58.0836 | 51.1188 | 42.147 | 20.2298 | 3.2913
Water Power | (㎾) | 0 | 0.56805 | 1.0275 | 1.4277 | 1.4982 | 1.374 | 0.82436 | 0.15102
Shaft Power | (㎾) | 0.85498 | 1.3762 | 1.8176 | 2.147 | 2.1945 | 2.1272 | 1.8878 | 1.7956
Pump Eff. | (%) | 0 | 41.278 | 56.5319 | 66.4996 | 68.2677 | 64.5919 | 43.6672 | 8.4106
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.75 | 4.31 | 4.9 | 5.45 | 5.53 | 5.41 | 4.98 | 4.85
Motor Input | (㎾) | 1.168 | 1.88 | 2.483 | 2.933 | 2.998 | 2.906 | 2.579 | 2.453
Motor Eff. | (%) | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 58 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 73.2 | Maker | FRANKLIN | Turbin | 58 | 43
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-8-9_MF4-3033 |  | Customer |  |  |  | 2 |  | 06/09/09
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(8-15)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50.5 | 100.5 | 150.2 | 182.2 | 200 | 250 | 283.3
Dis. Head | (m) | 125 | 113 | 103 | 93 | 80 | 68 | 35 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.022888 | 0.090647 | 0.20247 | 0.29793 | 0.35899 | 0.56092 | 0.7203
Total Head | (m) | 126 | 114.0229 | 104.0906 | 94.2025 | 81.2979 | 69.359 | 36.5609 | 3.7203
Water Power | (㎾) | 0 | 0.93858 | 1.7052 | 2.3063 | 2.4144 | 2.2611 | 1.4899 | 0.1718
Shaft Power | (㎾) | 1.5417 | 2.4364 | 3.227 | 3.7859 | 3.85 | 3.7457 | 3.3404 | 3.1583
Pump Eff. | (%) | 0 | 38.5227 | 52.8411 | 60.9189 | 62.7132 | 60.3646 | 44.6006 | 5.4396
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 6.21 | 7.11 | 8.24 | 9.15 | 9.26 | 9.07 | 8.42 | 8.15
Motor Input | (㎾) | 1.997 | 3.156 | 4.18 | 4.904 | 4.987 | 4.852 | 4.327 | 4.091
Motor Eff. | (%) | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 3.7 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 95 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 10.8 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 77.2 | Maker | FRANKLIN | Turbin | 42 | 39
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-8-15_MF4-5033 |  | Customer |  |  |  | 2 |  | 06/09/12
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## Test Report(8-25)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50.2 | 100.8 | 150.6 | 175.8 | 195.8 | 250 | 285.1
Dis. Head | (m) | 208 | 190 | 174 | 157 | 140 | 120 | 58 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0092637 | 0.037351 | 0.083374 | 0.11361 | 0.14093 | 0.22975 | 0.2988
Total Head | (m) | 209 | 191.0093 | 175.0374 | 158.0834 | 141.1136 | 121.1409 | 59.2298 | 3.2988
Water Power | (㎾) | 0 | 1.563 | 2.8759 | 3.8806 | 4.0437 | 3.8663 | 2.4136 | 0.1533
Shaft Power | (㎾) | 2.2274 | 3.6726 | 4.9543 | 5.7972 | 5.9104 | 5.7276 | 5.0209 | 4.8226
Pump Eff. | (%) | 0 | 42.5569 | 58.0492 | 66.9397 | 68.4164 | 67.5023 | 48.0713 | 3.1788
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 8.16 | 10.12 | 12.28 | 13.85 | 14.03 | 13.71 | 12.4 | 12.03
Motor Input | (㎾) | 3.01 | 4.963 | 6.695 | 7.834 | 7.987 | 7.74 | 6.785 | 6.517
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 130 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 160 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 16 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | FRANKLIN | Turbin | 58 | 43
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PSS-8-25_MF4-7533 |  | Customer |  |  |  | 2 |  | 06/09/14
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification