## Datasheet(PS-1-20)
Submersible Motor Pump Data Sheet
1 | Model | PS-1-20_MS4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 130 | m | Discharge Piece | STS304
10 | Rated Capacity | 16 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 190 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 42 | % | Pump Shaft | STS304
14 | Min. Flow | 10 | ℓ/min | Coupling | STS304
15 | Max. Flow | 25 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 10.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 20 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 499 | mm | Pump | 4.9 | kg
37 | Motor | 295 | mm | Motor | 10.6 | kg
38 | Total | 794 | mm | Total | 15.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PS-1-20)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-1-20_MS4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 130 | m | Discharge Piece | STS304
10 | Rated Capacity | 16 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 190 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 42 | % | Pump Shaft | STS304
14 | Min. Flow | 10 | ℓ/min | Coupling | STS304
15 | Max. Flow | 25 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 3.1 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 20 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 499 | mm | Pump | 4.9 | kg
37 | Motor | 265 | mm | Motor | 8.3 | kg
38 | Total | 764 | mm | Total | 13.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PS-1-20 | MS4-1012 | 20 |  |  | 1 |  | 1 | 220 | 60
| MS4-1033 | [5 empty] | 3 | 380 | 60
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PS-1-20 | MS4-1012 | 499 |  |  | 295 |  |  | 794
| MS4-1033 |  |  |  | 265 |  |  | 764
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PS-1-20 | MS4-1012 | 4.9 |  |  | 10.6 |  |  | 15.5
| MS4-1033 |  |  |  | 8.3 |  |  | 13.2
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 1 1/4"
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PS-1 Series
T.L
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge |  |  | STS304
2 | Valve Casing |  |  | STS304
4 | Valve Cone |  |  | STS304
6 | Valve Retaining Ring |  |  | STS304
8 | Upper Bearing Spider |  |  | STS304
12 | Diffuser |  |  | Polycarbonate
13 | Bowl |  |  | STS304
18 | Impeller |  |  | nPPO
24 | Stop Ring |  |  | STS304
34 | Strainer |  |  | STS304
36 | Suction Interconnector |  |  | STS304
40 | Pump Shaft/ Coupling |  |  | STS304
41 | Shaft Retaining Ring |  |  | STS304
42 | Shaft Sleeve |  |  | STS304
42A | Shaft Sleeve |  |  | STS304
48 | Casing |  |  | STS304
52 | Cable Guard |  |  | STS304
86 | O-ring |  |  | NBR
87 | O-ring |  |  | NBR
88 | Screw |  |  | STS304
89 | Screw |  |  | STS304
90 | Washer |  |  | STS304
91 | Washer |  |  | STS304
92 | Bearing |  |  | STS304
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PS-1 Series
36
34
89
42A
90
52
89
40
2
48
13
12
18
41
8
24
92
6
88
42
91
87
86
4
1

## PS-1-20_MS4-1012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 10.4 | 17.3 | 20.4 | 25.1 | 33.3
Dis. Head | (m) | 198 | 165 | 130 | 105 | 75.5 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0023699 | 0.0065577 | 0.0091184 | 0.013804 | 0.024297
Total Head | (m) | 199 | 166.0024 | 131.0066 | 106.0091 | 76.5138 | 3.5243
Water Power | (㎾) | 0 | 0.28141 | 0.36943 | 0.3525 | 0.31304 | 0.01913
Shaft Power | (㎾) | 0.68145 | 0.92276 | 1.029 | 1.0703 | 1.0762 | 1.0644
Pump Eff. | (%) | 0 | 30.4963 | 35.9028 | 32.9361 | 29.0887 | 1.7973
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.85 | 9.31 | 10.02 | 10.28 | 10.32 | 10.26
Motor Input | (㎾) | 1.155 | 1.564 | 1.744 | 1.814 | 1.824 | 1.804
Motor Eff. | (%) | 59 | 59 | 59 | 59 | 59 | 59
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 16 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 130 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 10.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 59 | Maker | SUMOTO | Turbin | 0
Item No. |  |  | Serial No. | X2 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-1-20_MS4-1012 |  | Customer |  |  |  | 2 |  | 2012.05.29
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-1-20_MS4-1033(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 10.5 | 17.3 | 20.1 | 24.9 | 32.3
Dis. Head | (m) | 195.5 | 165 | 130 | 104 | 74 | 2.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0024157 | 0.0065577 | 0.0088522 | 0.013585 | 0.022859
Total Head | (m) | 196.5 | 166.0024 | 131.0066 | 105.0089 | 75.0136 | 3.5229
Water Power | (㎾) | 0 | 0.28411 | 0.36943 | 0.34404 | 0.30446 | 0.018548
Shaft Power | (㎾) | 0.66999 | 0.89976 | 1.0074 | 1.0336 | 1.0481 | 1.0371
Pump Eff. | (%) | 0 | 31.5765 | 36.6712 | 33.285 | 29.0483 | 1.7885
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.42 | 2.76 | 2.94 | 2.99 | 3.02 | 3
Motor Input | (㎾) | 0.971 | 1.304 | 1.46 | 1.498 | 1.519 | 1.503
Motor Eff. | (%) | 69 | 69 | 69 | 69 | 69 | 69
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 16 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 130 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 3.1 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 69 | Maker | SUMOTO | Turbin | 0
Item No. |  |  | Serial No. | X1 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-1-20_MS4-1033 |  | Customer |  |  |  | 2 |  | 2012.05.25
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification