## Datasheet(13-5)
Submersible Motor Pump Data Sheet
1 | Model | PS-13-5_MS4-2012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 25 | m | Discharge Piece | STS304
10 | Rated Capacity | 200 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 40 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 54 | % | Pump Shaft | STS304
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 250 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 13.5 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 430 | mm | Pump | 4.4 | kg
37 | Motor | 375 | mm | Motor | 14 | kg
38 | Total | 805 | mm | Total | 18.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(13-5)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-13-5_MF4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 25 | m | Discharge Piece | STS304
10 | Rated Capacity | 200 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 40 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 54 | % | Pump Shaft | STS304
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 250 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 4.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 430 | mm | Pump | 4.4 | kg
37 | Motor | 340 | mm | Motor | 11.4 | kg
38 | Total | 770 | mm | Total | 15.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(13-7)
Submersible Motor Pump Data Sheet
1 | Model | PS-13-7_MS4-3012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 35 | m | Discharge Piece | STS304
10 | Rated Capacity | 200 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 60 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 54 | % | Pump Shaft | STS304
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 280 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 16.9 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 534 | mm | Pump | 5.3 | kg
37 | Motor | 430 | mm | Motor | 16.4 | kg
38 | Total | 964 | mm | Total | 21.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(13-7)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-13-7_MS4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 35 | m | Discharge Piece | STS304
10 | Rated Capacity | 200 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 60 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 54 | % | Pump Shaft | STS304
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 280 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 6.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 534 | mm | Pump | 5.3 | kg
37 | Motor | 375 | mm | Motor | 14.2 | kg
38 | Total | 909 | mm | Total | 19.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(13-11)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-13-11_MS4-5533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 55 | m | Discharge Piece | STS304
10 | Rated Capacity | 200 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 95 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 54 | % | Pump Shaft | STS304
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 280 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 11.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 11 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 742 | mm | Pump | 7.2 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 1297 | mm | Total | 30.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(13-17)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-13-17_MF4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 95 | m | Discharge Piece | STS304
10 | Rated Capacity | 200 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 145 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 54 | % | Pump Shaft | STS304
14 | Min. Flow | 100 | ℓ/min | Coupling | STS304
15 | Max. Flow | 280 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 15.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1092 | mm | Pump | 10.1 | kg
37 | Motor | 675 | mm | Motor | 29.4 | kg
38 | Total | 1767 | mm | Total | 39.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PS-13-5 | MS4-2012 | 5 |  |  | 2 |  | 1 | 220 | 60
| MS4-2033 | [5 empty] | 3 | 380 | 60
PS-13-7 | MS4-3012 | 7 |  |  | 3 |  | 1 | 220 | 60
| MS4-3033 | [5 empty] | 3 | 380 | 60
PS-13-11 | MS4-5033 | 11 |  |  | 5 |  | 3 | 380 | 60
PS-13-17 | MS4-7533 | 17 |  |  | 7 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PS-13-5 | MS4-2012 | 430 |  |  | 375 |  |  | 805
| MS4-2033 |  |  |  | 340 |  |  | 770
PS-13-7 | MS4-3012 | 534 |  |  | 430 |  |  | 964
| MS4-3033 |  |  |  | 375 |  |  | 909
PS-13-11 | MS4-5533 | 742 |  |  | 555 |  |  | 1297
PS-13-17 | MS4-7533 | 1092 |  |  | 675 |  |  | 1767
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PS-13-5 | MS4-2012 | 4.4 |  |  | 14 |  |  | 18.4
| MS4-2033 |  |  |  | 11.4 |  |  | 15.8
PS-13-7 | MS4-3012 | 5.3 |  |  | 16.4 |  |  | 21.7
| MS4-3033 |  |  |  | 14.2 |  |  | 19.5
PS-13-11 | MS4-5033 | 7.2 |  |  | 23.4 |  |  | 30.6
PS-13-17 | MS4-7533 | 10.1 |  |  | 29.4 |  |  | 39.5
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 2"
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PS-13 Series
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge |  |  | STS304
2 | Valve Casing |  |  | STS304
4 | Valve Cone |  |  | STS304
6 | Valve Retaining Ring |  |  | STS304
9 | Adapter Ring |  |  | STS304
10 | Bearing Spider |  |  | STS304
12 | Diffuser |  |  | Polycarbonate
13 | Bowl |  |  | STS304
18 | Impeller |  |  | nPPO
24 | Stop Ring |  |  | STS304
34 | Strainer |  |  | STS304
36 | Suction Interconnector |  |  | STS304
40 | Pump Shaft/ Coupling |  |  | STS304
41 | Shaft Retaining Ring |  |  | STS304
42 | Shaft Sleeve |  |  | STS304
42B | Shaft Sleeve |  |  | STS304
48 | Casing |  |  | STS304
52 | Cable Guard |  |  | STS304
86 | O-ring |  |  | NVR
87 | O-ring |  |  | NVR
88 | Screw |  |  | STS304
89 | Washer |  |  | STS304
90 | Bearing |  |  | STS304
92 | Washer |  |  | STS304
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PS-13 Series
24
42
41
87
86
4
36
88
34
89
48
42B
13
18
12
92
90
88
52
40
10
9
6
2
1

## PS-13-5_MS4-2012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 60.4 | 120.2 | 187.7 | 240 | 300.2 | 336.3
Dis. Head | (m) | 44.5 | 41 | 37 | 29 | 21.5 | 10.2 | 1.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013411 | 0.053111 | 0.12951 | 0.21174 | 0.33128 | 0.41575
Total Head | (m) | 45.5 | 42.0134 | 38.0531 | 30.1295 | 22.7117 | 11.5313 | 2.9158
Water Power | (㎾) | 0 | 0.41363 | 0.74556 | 0.92182 | 0.88848 | 0.56426 | 0.15983
Shaft Power | (㎾) | 1.1968 | 1.3138 | 1.4464 | 1.6232 | 1.6803 | 1.6483 | 1.5932
Pump Eff. | (%) | 0 | 31.4845 | 51.5473 | 56.7914 | 52.8771 | 34.2322 | 10.0319
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 9.56 | 10.24 | 11 | 12.1 | 12.46 | 12.24 | 11.88
Motor Input | (㎾) | 1.76 | 1.932 | 2.127 | 2.387 | 2.471 | 2.424 | 2.343
Motor Eff. | (%) | 68 | 68 | 68 | 68 | 68 | 68 | 68
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 220 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 25 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 13.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-13-5_MS4-2012 |  | Customer |  |  |  | 2 |  | 2011.05.23
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-13-5_MS4-2033(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 60.8 | 120.6 | 178.8 | 260 | 330
Dis. Head | (m) | 43 | 39.5 | 36 | 29 | 16 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013589 | 0.053466 | 0.11752 | 0.2485 | 0.40032
Total Head | (m) | 43.5 | 40.0136 | 36.5535 | 29.6175 | 16.7485 | 0.90032
Water Power | (㎾) | 0 | 0.39655 | 0.71856 | 0.86318 | 0.7098 | 0.048428
Shaft Power | (㎾) | 1.1285 | 1.2595 | 1.4038 | 1.5806 | 1.6635 | 1.5725
Pump Eff. | (%) | 0 | 31.4853 | 51.1876 | 54.6098 | 42.6686 | 3.0797
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.41 | 3.61 | 3.85 | 4.16 | 4.31 | 4.15
Motor Input | (㎾) | 1.525 | 1.702 | 1.897 | 2.136 | 2.248 | 2.125
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 25 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-13-5_MS4-2033 |  | Customer |  |  |  | 2 |  | 2011.01.18
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-13-7_MS4-3012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 60.6 | 120.7 | 188.8 | 240 | 300.4 | 344.4
Dis. Head | (m) | 63.5 | 58.5 | 53 | 42 | 31.8 | 16.2 | 2
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0135 | 0.053554 | 0.13103 | 0.21174 | 0.33173 | 0.43602
Total Head | (m) | 64.5 | 59.5135 | 54.0536 | 43.131 | 33.0117 | 17.5317 | 3.436
Water Power | (㎾) | 0 | 0.58786 | 1.0635 | 1.3273 | 1.2914 | 0.85844 | 0.19289
Shaft Power | (㎾) | 1.6429 | 1.8126 | 2.0214 | 2.2677 | 2.3373 | 2.2727 | 2.1605
Pump Eff. | (%) | 0 | 32.4315 | 52.6106 | 58.531 | 55.2521 | 37.7718 | 8.9278
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 10.62 | 11.77 | 13.05 | 14.76 | 15.27 | 14.88 | 14.11
Motor Input | (㎾) | 2.314 | 2.553 | 2.847 | 3.194 | 3.292 | 3.201 | 3.043
Motor Eff. | (%) | 71 | 71 | 71 | 71 | 71 | 71 | 71
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 220 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 35 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 16.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 71 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-13-7_MS4-3012 |  | Customer |  |  |  | 2 |  | 2011.05.24
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-13-7_MS4-3033(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 70 | 140 | 206 | 281 | 356.6
Dis. Head | (m) | 64 | 58 | 52 | 40 | 24 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.018013 | 0.07205 | 0.156 | 0.29026 | 0.46746
Total Head | (m) | 65 | 59.018 | 53.0721 | 41.156 | 25.2903 | 1.4675
Water Power | (㎾) | 0 | 0.6734 | 1.2111 | 1.3819 | 1.1584 | 0.085297
Shaft Power | (㎾) | 1.6575 | 1.8458 | 2.1157 | 2.3805 | 2.4143 | 2.2612
Pump Eff. | (%) | 0 | 36.4836 | 57.2423 | 58.0523 | 47.9805 | 3.7721
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 5.25 | 5.56 | 5.97 | 6.39 | 6.42 | 6.18
Motor Input | (㎾) | 2.21 | 2.461 | 2.821 | 3.174 | 3.219 | 3.015
Motor Eff. | (%) | 75 | 75 | 75 | 75 | 75 | 75
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 35 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 75 | Maker | 수모터 | Turbin | 0
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-13-7_MS4-3033 |  | Customer |  |  |  | 2 |  | 2010.11.11
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-13-11_MS4-5533
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (㎥/min) | 0 | 0.07 | 0.13 | 0.17 | 0.2 | 0.22 | 0.27 | 0.31 | 0.31 | 0.34
Dis. Head | (m) | 98 | 90.5 | 82 | 73.5 | 64 | 58 | 43 | 26.5 | 26.5 | 12
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.018013 | 0.062125 | 0.10624 | 0.14704 | 0.17792 | 0.26798 | 0.35327 | 0.35327 | 0.42495
Total Head | (m) | 99.65 | 92.168 | 83.7121 | 75.2562 | 65.797 | 59.8279 | 44.918 | 28.5033 | 28.5033 | 14.0749
Water Power | (kW) | 0 | 1.0516 | 1.7739 | 2.0854 | 2.145 | 2.1454 | 1.9768 | 1.4403 | 1.4403 | 0.78003
Shaft Power | (kW) | 2.5641 | 2.9799 | 3.3726 | 3.6652 | 3.8346 | 3.8962 | 3.9039 | 3.8038 | 4.4429 | 3.6883
Pump Eff. | (%) | 0 | 35.291 | 52.5962 | 56.8959 | 55.9376 | 55.0647 | 50.6376 | 37.864 | 32.4173 | 21.1489
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.25 | 7.92 | 8.6 | 9.11 | 9.4 | 9.51 | 9.54 | 9.36 | 10.51 | 9.14
Motor Input | (kW) | 3.33 | 3.87 | 4.38 | 4.76 | 4.98 | 5.06 | 5.07 | 4.94 | 5.77 | 4.79
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.22 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 4.0 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 55 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 |  | 50 | 1.65
Efficiency |  | (%) | Volt.(v) | 380 | Current(A) | 11.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 77 | M/T Maker | sumoto | MAGNET | 20 | 18.5
Item No. |  |  | Serial No. |  | Inspector | JUNG.Y.J | Run (Hr) | B/R (℃) | Test Date
Model | PS-13-11_MS4-5533 |  | Customer |  |  |  | 2 | 0 | 2011.05.11
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-13-17_MS4-7533
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 80 | 160 | 200 | 280 | 370
Dis. Head | (m) | 150 | 136.5 | 118 | 100 | 63 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023527 | 0.094106 | 0.14704 | 0.2882 | 0.50325
Total Head | (m) | 151.5 | 138.0235 | 119.5941 | 101.647 | 64.7882 | 2.0032
Water Power | (㎾) | 0 | 1.7998 | 3.119 | 3.3137 | 2.9569 | 0.12082
Shaft Power | (㎾) | 3.9546 | 4.6254 | 5.46 | 5.8656 | 5.9826 | 5.3976
Pump Eff. | (%) | 0 | 38.9118 | 57.1248 | 56.4937 | 49.4256 | 2.2383
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 10.62 | 11.72 | 13.18 | 13.97 | 14.13 | 13.06
Motor Input | (㎾) | 5.07 | 5.93 | 7 | 7.52 | 7.67 | 6.92
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 200 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 95 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 15.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | 수모터 | Turbin | 0
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-13-17_MS4-7533 |  | Customer |  |  |  | 2 |  | 2010.11.12
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification