## Datasheet(18-5)
Submersible Motor Pump Data Sheet
1 | Model | PS-18-5_MS4-3012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 22 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 40 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 45 | % | Pump Shaft | STS304
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 400 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 16.9 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 472 | mm | Pump | 4.4 | kg
37 | Motor | 430 | mm | Motor | 16.4 | kg
38 | Total | 902 | mm | Total | 20.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(18-5)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-18-5_MS4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 22 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 40 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 45 | % | Pump Shaft | STS304
14 | Min. Flow | 150 | ℓ/min | Coupling | STS304
15 | Max. Flow | 400 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 6.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 5 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 472 | mm | Pump | 4.4 | kg
37 | Motor | 375 | mm | Motor | 14.2 | kg
38 | Total | 847 | mm | Total | 18.6 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(18-9)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-18-9_MS4-5533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 45 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 75 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 54 | % | Pump Shaft | STS304
14 | Min. Flow | 170 | ℓ/min | Coupling | STS304
15 | Max. Flow | 430 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 6.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 9 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 743 | mm | Pump | 6.9 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 1298 | mm | Total | 30.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(18-14)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-18-14_MS4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 70 | m | Discharge Piece | STS304
10 | Rated Capacity | 300 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 115 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 54 | % | Pump Shaft | STS304
14 | Min. Flow | 170 | ℓ/min | Coupling | STS304
15 | Max. Flow | 430 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 15.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 14 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 1081 | mm | Pump | 9.9 | kg
37 | Motor | 675 | mm | Motor | 29.4 | kg
38 | Total | 1756 | mm | Total | 39.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PS-18-5 | MS4-3012 | 5 |  |  | 3 |  | 1 | 220 | 60
| MS4-3033 | [5 empty] | 3 | 380 | 60
PS-18-9 | MS4-5533 | 9 |  |  | 5.5 |  | 3 | 380 | 60
PS-18-14 | MS4-7533 | 14 |  |  | 7.5 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PS-18-5 | MS4-3012 | 472 |  |  | 430 |  |  | 902
| MS4-3033 |  |  |  | 375 |  |  | 847
PS-18-9 | MS4-5533 | 743 |  |  | 555 |  |  | 1298
PS-18-14 | MS4-7533 | 1081 |  |  | 675 |  |  | 1756
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PS-18-5 | MS4-3012 | 3.7 |  |  | 16.4 |  |  | 20.1
| MS4-3033 |  |  |  | 14.2 |  |  | 17.9
PS-18-9 | MS4-5533 | 6.9 |  |  | 23.4 |  |  | 30.3
PS-18-14 | MS4-7533 | 9.9 |  |  | 29.4 |  |  | 39.3
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 2"
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PS-18 Series
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge |  |  | STS304
2 | Valve Casing |  |  | STS304
4 | Valve Cone |  |  | STS304
6 | Valve Retaining Ring |  |  | STS304
9 | Adapter Ring |  |  | STS304
12 | Diffuser |  |  | Polycarbonate
13 | Bowl |  |  | STS304
18 | Impeller |  |  | nPPO
24 | Stop Ring |  |  | STS304
34 | Strainer |  |  | STS304
36 | Suction Interconnector |  |  | STS304
40 | Pump shaft/ Coupling |  |  | STS304
41 | Shaft Retaining Ring |  |  | STS304
42 | Shaft Sleeve |  |  | STS304
42A | Shaft Sleeve |  |  | STS304
42B | Shaft Sleeve |  |  | STS304
48 | Casing |  |  | STS304
52 | Cable Guard |  |  | STS304
86 | O-ring |  |  | NVR
87 | O-ring |  |  | NVR
88 | Screw |  |  | STS304
89 | Washer |  |  | STS304
90 | Bearing |  |  | STS304
92 | Washer |  |  | STS304
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PS-18 Series
87
86
4
92
42A
52
88
40
42B
13
18
12
24
9
6
2
1
90
42
41
88
36
34
89
48

## PS-18-5_MS4-3012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 80.6 | 160.2 | 226.2 | 320.2 | 401 | 491.6
Dis. Head | (m) | 42 | 38.2 | 33.8 | 29 | 22 | 13.8 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.023881 | 0.094342 | 0.18809 | 0.3769 | 0.59111 | 0.88839
Total Head | (m) | 43 | 39.2239 | 34.8943 | 30.1881 | 23.3769 | 15.3911 | 5.8884
Water Power | (㎾) | 0 | 0.51532 | 0.91118 | 1.1131 | 1.2201 | 1.006 | 0.47184
Shaft Power | (㎾) | 2.1265 | 2.1527 | 2.2372 | 2.2699 | 2.365 | 2.3707 | 2.4019
Pump Eff. | (%) | 0 | 23.9379 | 40.7285 | 49.036 | 51.5897 | 42.4353 | 19.6443
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 13.62 | 13.84 | 14.38 | 14.66 | 15.35 | 15.35 | 15.57
Motor Input | (㎾) | 2.995 | 3.032 | 3.151 | 3.197 | 3.331 | 3.339 | 3.383
Motor Eff. | (%) | 71 | 71 | 71 | 71 | 71 | 71 | 71
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 22 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 16.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 71 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-18-5_MS4-3012 |  | Customer |  |  |  | 2 |  | 2011.05.24
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-18-5_MS4-3033(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 100 | 180 | 221.6 | 300 | 400.8 | 483.5
Dis. Head | (m) | 42 | 37.5 | 32 | 29 | 23 | 12.5 | 3
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.03676 | 0.1191 | 0.18052 | 0.33084 | 0.59052 | 0.85935
Total Head | (m) | 42.5 | 38.0368 | 32.6191 | 29.6805 | 23.8308 | 13.5905 | 4.3594
Water Power | (㎾) | 0 | 0.62 | 0.95704 | 1.0721 | 1.1653 | 0.88787 | 0.34356
Shaft Power | (㎾) | 2.2088 | 2.256 | 2.322 | 2.3205 | 2.4315 | 2.4728 | 2.49
Pump Eff. | (%) | 0 | 27.4822 | 41.2164 | 46.2006 | 47.9263 | 35.9063 | 13.7977
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 6.14 | 6.21 | 6.31 | 6.31 | 6.48 | 6.56 | 6.59
Motor Input | (㎾) | 2.945 | 3.008 | 3.096 | 3.094 | 3.242 | 3.297 | 3.32
Motor Eff. | (%) | 75 | 75 | 75 | 75 | 75 | 75 | 75
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 22 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 75 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-18-5_MS4-3033 |  | Customer |  |  |  | 2 |  | 2011.01.18
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-18-9_MS4-5533
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (㎥/min) | 0 | 0.13 | 0.18 | 0.23 | 0.3 | 0.36 | 0.45 | 0.5
Dis. Head | (m) | 77 | 66.8 | 60.5 | 55 | 47 | 38 | 23.5 | 14
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.062125 | 0.1191 | 0.19446 | 0.33084 | 0.47641 | 0.7444 | 0.91901
Total Head | (m) | 78.65 | 68.5121 | 62.2691 | 56.8445 | 48.9808 | 40.1264 | 25.8944 | 16.569
Water Power | (kW) | 0 | 1.4518 | 1.827 | 2.1311 | 2.3952 | 2.3546 | 1.8994 | 1.3504
Shaft Power | (kW) | 3.9424 | 4.1503 | 4.1734 | 4.2273 | 4.4275 | 4.4814 | 4.5276 | 4.5045
Pump Eff. | (%) | 0 | 34.9799 | 43.7767 | 50.4128 | 54.0974 | 52.542 | 41.9506 | 29.9783
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 9.58 | 9.96 | 10.04 | 10.1 | 10.48 | 10.6 | 10.67 | 10.62
Motor Input | (kW) | 5.12 | 5.39 | 5.42 | 5.49 | 5.75 | 5.82 | 5.88 | 5.85
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.3 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 4.0 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 45 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 |  | 50 | 1.65
Efficiency |  | (%) | Volt.(v) | 380 | Current(A) | 11.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 77 | M/T Maker | sumoto | MAGNET | 20 | 18.5
Item No. |  |  | Serial No. |  | Inspector | JUNG.Y.J | Run (Hr) | B/R (℃) | Test Date
Model | PS-18-9_MS4-5533 |  | Customer |  |  |  | 2 | 0 | 2011.05.11
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-18-14_MS4-7533(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 100.9 | 200.2 | 295.8 | 400.6 | 499.9
Dis. Head | (m) | 122 | 110 | 93.8 | 76 | 52 | 4
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.037425 | 0.14734 | 0.32164 | 0.58993 | 0.91864
Total Head | (m) | 122.5 | 110.5374 | 94.4473 | 76.8216 | 53.0899 | 5.4186
Water Power | (㎾) | 0 | 1.818 | 3.0821 | 3.704 | 3.4667 | 0.44153
Shaft Power | (㎾) | 6.1628 | 6.3118 | 6.4015 | 6.7111 | 6.7977 | 6.176
Pump Eff. | (%) | 0 | 28.803 | 48.1462 | 55.1918 | 50.9975 | 7.1491
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 14.54 | 14.82 | 14.93 | 15.51 | 15.7 | 14.55
Motor Input | (㎾) | 7.901 | 8.092 | 8.207 | 8.604 | 8.715 | 7.918
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 300 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 5.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 70 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 15.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 78 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-18-14_MS4-7533 |  | Customer |  |  |  | 2 |  | 2011.01.19
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification