## Datasheet(PS-2-12)
Submersible Motor Pump Data Sheet
1 | Model | PS-2-12_MS4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 75 | m | Discharge Piece | STS304
10 | Rated Capacity | 40 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 115 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 59 | % | Pump Shaft | STS304
14 | Min. Flow | 60 | ℓ/min | Coupling | STS304
15 | Max. Flow | 30 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 10.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 12 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 359 | mm | Pump | 3.6 | kg
37 | Motor | 295 | mm | Motor | 10.6 | kg
38 | Total | 654 | mm | Total | 14.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PS-2-12)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-2-12_MS4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 75 | m | Discharge Piece | STS304
10 | Rated Capacity | 40 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 115 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 59 | % | Pump Shaft | STS304
14 | Min. Flow | 60 | ℓ/min | Coupling | STS304
15 | Max. Flow | 30 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 3.1 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 12 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 359 | mm | Pump | 3.6 | kg
37 | Motor | 265 | mm | Motor | 8.3 | kg
38 | Total | 624 | mm | Total | 11.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PS-2-12 | MS4-1012 | 12 |  |  | 1 |  | 1 | 220 | 60
| MS4-1033 | [5 empty] | 3 | 380 | 60
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PS-2-12 | MS4-1012 | 359 |  |  | 295 |  |  | 654
| MS4-1033 |  |  |  | 265 |  |  | 624
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PS-2-12 | MS4-1012 | 3.6 |  |  | 10.6 |  |  | 14.2
| MS4-1033 |  |  |  | 8.3 |  |  | 11.9
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 1 1/4"
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PS-1 Series
T.L
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge |  |  | STS304
2 | Valve Casing |  |  | STS304
4 | Valve Cone |  |  | STS304
6 | Valve Retaining Ring |  |  | STS304
8 | Upper Bearing Spider |  |  | STS304
12 | Diffuser |  |  | Polycarbonate
13 | Bowl |  |  | STS304
18 | Impeller |  |  | nPPO
24 | Stop Ring |  |  | STS304
34 | Strainer |  |  | STS304
36 | Suction Interconnector |  |  | STS304
40 | Pump Shaft/ Coupling |  |  | STS304
41 | Shaft Retaining Ring |  |  | STS304
42 | Shaft Sleeve |  |  | STS304
42A | Shaft Sleeve |  |  | STS304
48 | Casing |  |  | STS304
52 | Cable Guard |  |  | STS304
86 | O-ring |  |  | NBR
87 | O-ring |  |  | NBR
88 | Screw |  |  | STS304
89 | Screw |  |  | STS304
90 | Washer |  |  | STS304
91 | Washer |  |  | STS304
92 | Bearing |  |  | STS304
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PS-2 Series
36
34
89
42A
90
52
89
40
2
48
13
12
18
41
8
24
92
6
88
42
91
87
86
4
1

## PS-2-12_MS4-1012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.3 | 35 | 43.2 | 55.4 | 77
Dis. Head | (m) | 114 | 102 | 86 | 75 | 51 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0090292 | 0.026841 | 0.040891 | 0.067248 | 0.12991
Total Head | (m) | 115 | 103.009 | 87.0268 | 76.0409 | 52.0672 | 1.1299
Water Power | (㎾) | 0 | 0.34085 | 0.49649 | 0.53545 | 0.47018 | 0.014181
Shaft Power | (㎾) | 0.59 | 0.85786 | 1.013 | 1.0602 | 1.0756 | 0.98825
Pump Eff. | (%) | 0 | 39.7322 | 49.0102 | 50.5031 | 43.7143 | 1.435
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 7.39 | 8.92 | 10.04 | 10.38 | 10.41 | 9.77
Motor Input | (㎾) | 1 | 1.454 | 1.717 | 1.797 | 1.823 | 1.675
Motor Eff. | (%) | 59 | 59 | 59 | 59 | 59 | 59
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 40 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 75 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 10.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 59 | Maker | SUMOTO | Turbin | 0
Item No. |  |  | Serial No. | X1 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-2-12_MS4-1012 |  | Customer |  |  |  | 2 |  | 2012.05.26
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-2-12_MS4-1033 (380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.5 | 35.6 | 43.3 | 55.6 | 76.7
Dis. Head | (m) | 114 | 102 | 86 | 75 | 51 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.009208 | 0.027769 | 0.04108 | 0.067734 | 0.1289
Total Head | (m) | 115 | 103.0092 | 87.0278 | 76.0411 | 52.0677 | 1.1289
Water Power | (㎾) | 0 | 0.34421 | 0.505 | 0.53669 | 0.47188 | 0.014114
Shaft Power | (㎾) | 0.5796 | 0.82869 | 0.98463 | 1.026 | 1.0336 | 0.966
Pump Eff. | (%) | 0 | 41.5361 | 51.2888 | 52.3075 | 45.6531 | 1.461
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.33 | 2.67 | 2.92 | 2.99 | 3.01 | 2.89
Motor Input | (㎾) | 0.84 | 1.201 | 1.427 | 1.487 | 1.498 | 1.4
Motor Eff. | (%) | 69 | 69 | 69 | 69 | 69 | 69
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 40 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 75 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 3.1 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 69 | Maker | SUMOTO | Turbin | 0
Item No. |  |  | Serial No. | X2 | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-2-12_MS4-1033 |  | Customer |  |  |  | 2 |  | 2012.05.30
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification