## Datasheet(PS-3-10)
Submersible Motor Pump Data Sheet
1 | Model | PS-3-10_MS4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 65 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 90 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS304
14 | Min. Flow | 30 | ℓ/min | Coupling | STS304
15 | Max. Flow | 70 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 10.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 10 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 324 | mm | Pump | 3.2 | kg
37 | Motor | 295 | mm | Motor | 10.6 | kg
38 | Total | 619 | mm | Total | 13.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PS-3-10)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-3-10_MS4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 65 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 90 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS304
14 | Min. Flow | 30 | ℓ/min | Coupling | STS304
15 | Max. Flow | 70 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 3.1 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 10 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 324 | mm | Pump | 3.2 | kg
37 | Motor | 265 | mm | Motor | 8.3 | kg
38 | Total | 589 | mm | Total | 11.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PS-3-17)
Submersible Motor Pump Data Sheet
1 | Model | PS-3-17_MS4-2012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 120 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 155 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS304
14 | Min. Flow | 30 | ℓ/min | Coupling | STS304
15 | Max. Flow | 70 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 13.5 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 447 | mm | Pump | 4.3 | kg
37 | Motor | 375 | mm | Motor | 14 | kg
38 | Total | 822 | mm | Total | 18.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PS-3-17)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-3-17_MS4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 120 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 155 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS304
14 | Min. Flow | 30 | ℓ/min | Coupling | STS304
15 | Max. Flow | 70 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 4.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 17 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 447 | mm | Pump | 4.3 | kg
37 | Motor | 340 | mm | Motor | 11.4 | kg
38 | Total | 787 | mm | Total | 15.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PS-3-21)
Submersible Motor Pump Data Sheet
1 | Model | PS-3-21_MS4-3012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 155 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 195 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS304
14 | Min. Flow | 30 | ℓ/min | Coupling | STS304
15 | Max. Flow | 70 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 16.9 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 21 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 519 | mm | Pump | 5 | kg
37 | Motor | 430 | mm | Motor | 16.4 | kg
38 | Total | 949 | mm | Total | 21.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PS-3-21)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-3-21_MS4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 155 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 195 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS304
14 | Min. Flow | 30 | ℓ/min | Coupling | STS304
15 | Max. Flow | 70 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 6.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 21 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 519 | mm | Pump | 5 | kg
37 | Motor | 375 | mm | Motor | 14.2 | kg
38 | Total | 894 | mm | Total | 19.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(PS-3-35)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-3-35_MS4-5533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 240 | m | Discharge Piece | STS304
10 | Rated Capacity | 50 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 315 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 50 | % | Pump Shaft | STS304
14 | Min. Flow | 30 | ℓ/min | Coupling | STS304
15 | Max. Flow | 70 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 32 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 11.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 35 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 803 | mm | Pump | 7.6 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 1358 | mm | Total | 31 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PS-3-10 | MS4-1012 | 10 |  |  | 1 |  | 1 | 220 | 60
| MS4-1033 | [5 empty] | 3 | 380 | 60
PS-3-17 | MS4-2012 | 17 |  |  | 2 |  | 1 | 220 | 60
| MS4-2033 | [5 empty] | 3 | 380 | 60
PS-3-21 | MS4-3012 | 21 |  |  | 3 |  | 1 | 220 | 60
| MS4-3033 | [5 empty] | 3 | 380 | 60
PS-3-35 | MS4-5533 | 35 |  |  | 5.5 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PS-3-10 | MS4-1012 | 324 |  |  | 295 |  |  | 619
| MS4-1033 |  |  |  | 265 |  |  | 589
PS-3-17 | MS4-2012 | 447 |  |  | 375 |  |  | 822
| MS4-2033 |  |  |  | 340 |  |  | 787
PS-3-21 | MS4-3012 | 519 |  |  | 430 |  |  | 949
| MS4-3033 |  |  |  | 375 |  |  | 894
PS-3-35 | MS4-5533 | 803 |  |  | 555 |  |  | 1358
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PS-3-10 | MS4-1012 | 3.2 |  |  | 10.6 |  |  | 13.8
| MS4-1033 |  |  |  | 8.3 |  |  | 11.5
PS-3-17 | MS4-2012 | 4.3 |  |  | 14 |  |  | 18.3
| MS4-2033 |  |  |  | 11.4 |  |  | 15.7
PS-3-21 | MS4-3012 | 5 |  |  | 16.4 |  |  | 21.4
| MS4-3033 |  |  |  | 14.2 |  |  | 19.2
PS-3-35 | MS4-5533 | 7.6 |  |  | 23.4 |  |  | 31
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 1 1/4"
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PS-3 Series
T.L
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge |  |  | STS304
2 | Valve Casing |  |  | STS304
4 | Valve Cone |  |  | STS304
6 | Valve Retaining Ring |  |  | STS304
8 | Upper Bearing Spider |  |  | STS304
12 | Diffuser |  |  | STS304
13 | Bowl |  |  | STS304
18 | Impeller |  |  | nPPO
24 | Stop Ring |  |  | STS304
34 | Strainer |  |  | STS304
36 | Suction Interconnector |  |  | STS304
40 | Pump Shaft/ Coupling |  |  | STS304
41 | Shaft Retaining Ring |  |  | STS304
42 | Shaft Sleeve |  |  | STS304
42A | Shaft Sleeve |  |  | STS304
48 | Casing |  |  | STS304
52 | Cable Guard |  |  | STS304
86 | O-ring |  |  | NBR
87 | O-ring |  |  | NBR
88 | Screw |  |  | STS304
89 | Screw |  |  | STS304
90 | Washer |  |  | STS304
91 | Washer |  |  | STS304
92 | Bearing |  |  | STS304
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PS-3 Series
36
34
89
42A
90
52
89
40
2
48
13
12
18
41
8
24
92
6
88
42
91
87
86
4
1

## PS-3-10_MS4-1012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.2 | 40.4 | 48.2 | 60.2 | 80 | 92.1
Dis. Head | (m) | 93 | 88 | 76 | 69 | 56 | 26 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0089405 | 0.035762 | 0.050904 | 0.079406 | 0.14023 | 0.18586
Total Head | (m) | 94 | 89.0089 | 77.0358 | 70.0509 | 57.0794 | 27.1402 | 1.1859
Water Power | (㎾) | 0 | 0.29307 | 0.5073 | 0.55036 | 0.5601 | 0.35391 | 0.017802
Shaft Power | (㎾) | 0.56596 | 0.73472 | 0.91036 | 0.96432 | 1.0395 | 1.0826 | 1.0768
Pump Eff. | (%) | 0 | 39.8888 | 55.7245 | 57.0725 | 53.8807 | 32.6917 | 1.6532
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.72 | 7.76 | 9 | 9.39 | 9.94 | 10.28 | 10.23
Motor Input | (㎾) | 0.986 | 1.28 | 1.586 | 1.68 | 1.811 | 1.886 | 1.876
Motor Eff. | (%) | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 57.4
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 65 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 187 | Current(A) | 10.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 57.4 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-3-10_MS4-1012 |  | Customer |  |  |  | 2 |  | 2007.06.15
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-3-10_MS4-1033(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 49.5 | 70 | 85 | 95.7
Dis. Head | (m) | 93 | 84 | 69 | 46 | 21 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.053687 | 0.10736 | 0.15831 | 0.20067
Total Head | (m) | 93.5 | 84.5197 | 69.5537 | 46.6074 | 21.6583 | 0.70067
Water Power | (㎾) | 0 | 0.4133 | 0.56119 | 0.53179 | 0.30008 | 0.01093
Shaft Power | (㎾) | 0.5589 | 0.85422 | 1.0033 | 1.1109 | 1.1316 | 1.1254
Pump Eff. | (%) | 0 | 48.3835 | 55.937 | 47.8702 | 26.5178 | 0.9712
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.21 | 2.65 | 2.9 | 3.1 | 3.14 | 3.12
Motor Input | (㎾) | 0.81 | 1.238 | 1.454 | 1.61 | 1.64 | 1.631
Motor Eff. | (%) | 69 | 69 | 69 | 69 | 69 | 69
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 65 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 3.1 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 69 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-3-10_MS4-1033 |  | Customer |  |  |  | 2 |  | 2011.01.14
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-3-17_MS4-2012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.5 | 40 | 47.2 | 60 | 80 | 94.2
Dis. Head | (m) | 165 | 158.5 | 139 | 128 | 105 | 54 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.009208 | 0.035057 | 0.048814 | 0.078879 | 0.14023 | 0.19443
Total Head | (m) | 166 | 159.5092 | 140.0351 | 129.0488 | 106.0789 | 55.1402 | 1.1944
Water Power | (㎾) | 0 | 0.533 | 0.91303 | 0.99285 | 1.0375 | 0.71903 | 0.01834
Shaft Power | (㎾) | 0.96696 | 1.2798 | 1.5953 | 1.6918 | 1.8469 | 1.9564 | 2.6044
Pump Eff. | (%) | 0 | 41.6484 | 57.2331 | 58.6846 | 56.1732 | 36.7534 | 0.70419
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 8.4 | 9.96 | 11.83 | 12.44 | 13.44 | 14.18 | 13.96
Motor Input | (㎾) | 1.422 | 1.882 | 2.346 | 2.488 | 2.716 | 2.877 | 3.83
Motor Eff. | (%) | 68 | 68 | 68 | 68 | 68 | 68 | 68
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 120 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 187 | Current(A) | 13.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-3-17_MS4-2012 |  | Customer |  |  |  | 2 |  | 2011.05.18
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-3-17_MS4-2033(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.5 | 46.2 | 60.7 | 70.3 | 80.4 | 95.3
Dis. Head | (m) | 161 | 148 | 128 | 104 | 84.5 | 58 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.020383 | 0.046767 | 0.08073 | 0.10829 | 0.14164 | 0.199
Total Head | (m) | 161.5 | 148.5204 | 128.5468 | 104.5807 | 85.1083 | 58.6416 | 0.699
Water Power | (㎾) | 0 | 0.73837 | 0.96803 | 1.0347 | 0.97525 | 0.76851 | 0.010858
Shaft Power | (㎾) | 0.86802 | 1.477 | 1.7175 | 1.8537 | 1.9566 | 1.9514 | 1.904
Pump Eff. | (%) | 0 | 49.9898 | 56.3617 | 55.8198 | 49.845 | 39.3829 | 0.57027
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.07 | 4 | 4.43 | 4.68 | 4.87 | 4.87 | 4.78
Motor Input | (㎾) | 1.173 | 1.996 | 2.321 | 2.505 | 2.644 | 2.637 | 2.573
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 120 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-3-17_MS4-2033 |  | Customer |  |  |  | 2 |  | 2011.01.14
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-3-21_MS4-3012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 20.4 | 40.6 | 45 | 60.4 | 80.1 | 93.6
Dis. Head | (m) | 198 | 193 | 170 | 162 | 131 | 71 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091184 | 0.036117 | 0.044369 | 0.079934 | 0.14058 | 0.19196
Total Head | (m) | 199 | 194.0091 | 171.0361 | 163.0444 | 132.0799 | 72.1406 | 1.192
Water Power | (㎾) | 0 | 0.64512 | 1.1319 | 1.1959 | 1.3004 | 0.94189 | 0.018185
Shaft Power | (㎾) | 1.5194 | 1.8112 | 2.1761 | 2.2273 | 2.4147 | 2.4758 | 2.4424
Pump Eff. | (%) | 0 | 35.6181 | 52.0131 | 53.6949 | 53.8513 | 38.0443 | 0.74457
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 9.73 | 11.54 | 13.87 | 14.28 | 15.59 | 16.03 | 15.75
Motor Input | (㎾) | 2.14 | 2.551 | 3.065 | 3.137 | 3.401 | 3.487 | 3.44
Motor Eff. | (%) | 71 | 71 | 71 | 71 | 71 | 71 | 71
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 155 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 16.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 71 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-3-21_MS4-3012 |  | Customer |  |  |  | 2 |  | 2011.05.18
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-3-21_MS4-3033(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 48.9 | 60.6 | 70.4 | 80.3 | 98.4
Dis. Head | (m) | 201 | 188.5 | 162 | 140 | 116 | 85 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.01972 | 0.052393 | 0.080465 | 0.10859 | 0.14128 | 0.21215
Total Head | (m) | 201.5 | 189.0197 | 162.5524 | 140.5805 | 116.6086 | 85.6413 | 0.71215
Water Power | (㎾) | 0 | 0.92431 | 1.2957 | 1.3886 | 1.3381 | 1.121 | 0.011422
Shaft Power | (㎾) | 1.3838 | 2.0475 | 2.3977 | 2.5972 | 2.685 | 2.7172 | 2.6625
Pump Eff. | (%) | 0 | 45.1432 | 54.0363 | 53.4652 | 49.8364 | 41.2531 | 0.42901
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 5 | 5.89 | 6.42 | 6.73 | 6.9 | 6.96 | 6.87
Motor Input | (㎾) | 1.845 | 2.73 | 3.197 | 3.463 | 3.58 | 3.623 | 3.55
Motor Eff. | (%) | 75 | 75 | 75 | 75 | 75 | 75 | 75
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 50 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 155 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 32 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 75 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-3-21_MS4-3033 |  | Customer |  |  |  | 2 |  | 2011.01.15
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-3-35_MS4-5533
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (㎥/min) | 0 | 0.0342 | 0.05 | 0.0642 | 0.0745 | 0.0825 | 0.0897 | 0.095
Dis. Head | (m) | 324 | 300 | 250 | 200 | 150 | 100 | 50 | 10
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.025628 | 0.054777 | 0.090309 | 0.12161 | 0.14913 | 0.1763 | 0.19775
Total Head | (m) | 325.65 | 301.6756 | 251.7048 | 201.7403 | 151.7716 | 101.7991 | 51.8263 | 11.8477
Water Power | (kW) | 0 | 1.6817 | 2.0514 | 2.1111 | 1.843 | 1.3689 | 0.75776 | 0.18346
Shaft Power | (kW) | 2.7027 | 3.2417 | 3.7345 | 4.0733 | 4.2273 | 4.2889 | 4.2658 | 4.2119
Pump Eff. | (%) | 0 | 51.8777 | 54.9309 | 51.8285 | 43.5985 | 31.9183 | 17.7635 | 4.3558
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.48 | 8.36 | 9.22 | 9.84 | 10.11 | 10.21 | 10.19 | 10.08
Motor Input | (kW) | 3.51 | 4.21 | 4.85 | 5.29 | 5.49 | 5.57 | 5.54 | 5.47
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.05 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 4.0 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 240 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 |  | 32 | 1.65
Efficiency |  | (%) | Volt.(v) | 380 | Current(A) | 11.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 77 | M/T Maker | sumoto | MAGNET | 20 | 18.5
Item No. |  |  | Serial No. |  | Inspector | JUNG.Y.J | Run (Hr) | B/R (℃) | Test Date
Model | PS-3-35_MS4-5533 |  | Customer |  |  |  | 2 | 0 | 2011.05.06
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification