## Datasheet(5-7)
Submersible Motor Pump Data Sheet
1 | Model | PS-5-7_MS4-1012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 40 | m | Discharge Piece | STS304
10 | Rated Capacity | 90 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 60 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 52 | % | Pump Shaft | STS304
14 | Min. Flow | 50 | ℓ/min | Coupling | STS304
15 | Max. Flow | 110 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 10.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 320 | mm | Pump | 3.1 | kg
37 | Motor | 295 | mm | Motor | 10.6 | kg
38 | Total | 615 | mm | Total | 13.7 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-7)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-5-7_MS4-1033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 40 | m | Discharge Piece | STS304
10 | Rated Capacity | 90 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 60 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 52 | % | Pump Shaft | STS304
14 | Min. Flow | 50 | ℓ/min | Coupling | STS304
15 | Max. Flow | 110 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SOMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 0.75 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 3.1 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 153 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 7 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 320 | mm | Pump | 3.1 | kg
37 | Motor | 265 | mm | Motor | 8.3 | kg
38 | Total | 585 | mm | Total | 11.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-11)
Submersible Motor Pump Data Sheet
1 | Model | PS-5-11_MS4-2012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 60 | m | Discharge Piece | STS304
10 | Rated Capacity | 90 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 95 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 52 | % | Pump Shaft | STS304
14 | Min. Flow | 50 | ℓ/min | Coupling | STS304
15 | Max. Flow | 110 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 13.5 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 11 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 419 | mm | Pump | 3.9 | kg
37 | Motor | 375 | mm | Motor | 14 | kg
38 | Total | 794 | mm | Total | 17.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-11)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-5-11_MS4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 60 | m | Discharge Piece | STS304
10 | Rated Capacity | 90 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 95 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 52 | % | Pump Shaft | STS304
14 | Min. Flow | 50 | ℓ/min | Coupling | STS304
15 | Max. Flow | 110 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 4.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 11 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 419 | mm | Pump | 3.9 | kg
37 | Motor | 340 | mm | Motor | 11.4 | kg
38 | Total | 759 | mm | Total | 15.3 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-15)
Submersible Motor Pump Data Sheet
1 | Model | PS-5-15_MS4-3012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 90 | m | Discharge Piece | STS304
10 | Rated Capacity | 90 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 130 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 52 | % | Pump Shaft | STS304
14 | Min. Flow | 50 | ℓ/min | Coupling | STS304
15 | Max. Flow | 110 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 16.9 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 15 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 518 | mm | Pump | 4.7 | kg
37 | Motor | 430 | mm | Motor | 16.4 | kg
38 | Total | 948 | mm | Total | 21.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-15)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-5-15_MS4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 90 | m | Discharge Piece | STS304
10 | Rated Capacity | 90 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 130 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 52 | % | Pump Shaft | STS304
14 | Min. Flow | 50 | ℓ/min | Coupling | STS304
15 | Max. Flow | 110 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 6.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 15 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 518 | mm | Pump | 4.7 | kg
37 | Motor | 375 | mm | Motor | 14.2 | kg
38 | Total | 893 | mm | Total | 18.9 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(5-26)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-5-26_MS4-5533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 160 | m | Discharge Piece | STS304
10 | Rated Capacity | 90 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 225 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 52 | % | Pump Shaft | STS304
14 | Min. Flow | 50 | ℓ/min | Coupling | STS304
15 | Max. Flow | 110 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 40 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 11.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 26 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 826 | mm | Pump | 7.1 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 1381 | mm | Total | 30.5 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PS-5-7 | MS4-1012 | 7 |  |  | 1 |  | 1 | 220 | 60
| MS4-1033 | [5 empty] | 3 | 380 | 60
PS-5-11 | MS4-2012 | 11 |  |  | 2 |  | 1 | 220 | 60
| MS4-2033 | [5 empty] | 3 | 380 | 60
PS-5-15 | MS4-3012 | 15 |  |  | 3 |  | 1 | 220 | 60
| MS4-3033 | [5 empty] | 3 | 380 | 60
PS-5-26 | MS4-5533 | 26 |  |  | 5.5 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PS-5-7 | MS4-1012 | 320 |  |  | 295 |  |  | 615
| MS4-1033 |  |  |  | 265 |  |  | 585
PS-5-11 | MS4-2012 | 419 |  |  | 375 |  |  | 794
| MS4-2033 |  |  |  | 340 |  |  | 759
PS-5-15 | MS4-3012 | 518 |  |  | 430 |  |  | 948
| MS4-3033 |  |  |  | 375 |  |  | 893
PS-5-26 | MS4-5533 | 826 |  |  | 555 |  |  | 1381
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PS-5-7 | MS4-1012 | 3.1 |  |  | 10.6 |  |  | 13.7
| MS4-1033 |  |  |  | 8.3 |  |  | 11.4
PS-5-11 | MS4-2012 | 3.9 |  |  | 14 |  |  | 17.9
| MS4-2033 |  |  |  | 11.4 |  |  | 15.3
PS-5-15 | MS4-3012 | 4.7 |  |  | 16.4 |  |  | 21.1
| MS4-3033 |  |  |  | 14.2 |  |  | 18.9
PS-5-26 | MS4-5533 | 7.1 |  |  | 23.4 |  |  | 30.5
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 1 1/2"
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PS-5 Series
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge |  |  | STS304
2 | Valve Casing |  |  | STS304
4 | Valve Cone |  |  | STS304
6 | Valve Retaining Ring |  |  | STS304
8 | Upper Bearing Spider |  |  | STS304
12 | Diffuser |  |  | Polycarbonate
13 | Bowl |  |  | STS304
18 | Impeller |  |  | nPPO
24 | Stop Ring |  |  | STS304
34 | Strainer |  |  | STS304
36 | Suction Interconnector |  |  | STS304
40 | Pump Shaft/ Coupling |  |  | STS304
41 | Shaft Retaining Ring |  |  | STS304
42 | Shaft Sleeve |  |  | STS304
42A | Shaft Sleeve |  |  | STS304
48 | Casing |  |  | STS304
52 | Cable Guard |  |  | STS304
86 | O-ring |  |  | NBR
87 | O-ring |  |  | NBR
88 | Screw |  |  | STS304
89 | Screw |  |  | STS304
90 | Washer |  |  | STS304
91 | Washer |  |  | STS304
92 | Bearing |  |  | STS304
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PS-5 Series
36
34
89
42A
90
52
89
40
2
48
13
12
18
41
8
24
92
6
88
42
91
87
86
4
1

## PS-5-7_MS4-1012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.7 | 60.1 | 83.3 | 120.7 | 148.2
Dis. Head | (m) | 62 | 60.5 | 54 | 45 | 23 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0084586 | 0.032417 | 0.062274 | 0.13075 | 0.19711
Total Head | (m) | 63 | 61.5085 | 55.0324 | 46.0623 | 24.1307 | 1.1971
Water Power | (㎾) | 0 | 0.30779 | 0.53911 | 0.62543 | 0.47475 | 0.028918
Shaft Power | (㎾) | 0.57584 | 0.75697 | 0.88677 | 0.99828 | 1.0986 | 1.0779
Pump Eff. | (%) | 0 | 40.6614 | 60.7953 | 62.6507 | 43.2149 | 2.6828
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 6.72 | 7.79 | 8.63 | 9.43 | 10.2 | 10
Motor Input | (㎾) | 0.976 | 1.283 | 1.503 | 1.692 | 1.862 | 1.827
Motor Eff. | (%) | 59 | 59 | 59 | 59 | 59 | 59
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 90 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 40 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 10.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 59 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-5-7_MS4-1012 |  | Customer |  |  |  | 2 |  | 2011.05.19
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-5-7_MS4-1033(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.4 | 60.4 | 82.4 | 120.5 | 148.5
Dis. Head | (m) | 62 | 57.5 | 53 | 45 | 23 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014648 | 0.032741 | 0.060936 | 0.13031 | 0.19791
Total Head | (m) | 62.5 | 58.0146 | 53.5327 | 45.5609 | 23.6303 | 0.69791
Water Power | (㎾) | 0 | 0.38204 | 0.52704 | 0.61194 | 0.46413 | 0.016893
Shaft Power | (㎾) | 0.54786 | 0.78108 | 0.897 | 1.0095 | 1.1392 | 1.1357
Pump Eff. | (%) | 0 | 48.9115 | 58.7559 | 60.6197 | 40.7425 | 1.4874
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 2.18 | 2.51 | 2.71 | 2.9 | 3.15 | 3.14
Motor Input | (㎾) | 0.794 | 1.132 | 1.3 | 1.463 | 1.651 | 1.646
Motor Eff. | (%) | 69 | 69 | 69 | 69 | 69 | 69
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 90 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 0.75 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 40 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 3.1 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 69 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-5-7_MS4-1033 |  | Customer |  |  |  | 2 |  | 2011.01.15
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-5-11_MS4-2012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.1 | 60.5 | 85.3 | 120 | 150.6
Dis. Head | (m) | 100 | 98 | 89 | 75 | 43 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0081312 | 0.03285 | 0.065301 | 0.12924 | 0.20355
Total Head | (m) | 101 | 99.0081 | 90.0328 | 76.0653 | 44.1292 | 1.2035
Water Power | (㎾) | 0 | 0.48576 | 0.88786 | 1.0576 | 0.86317 | 0.029544
Shaft Power | (㎾) | 0.91936 | 1.173 | 1.4545 | 1.6558 | 1.8544 | 1.8244
Pump Eff. | (%) | 0 | 41.4121 | 61.0414 | 63.8727 | 46.548 | 1.6194
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 8.14 | 9.38 | 11 | 12.26 | 13.53 | 13.33
Motor Input | (㎾) | 1.352 | 1.725 | 2.139 | 2.435 | 2.727 | 2.683
Motor Eff. | (%) | 68 | 68 | 68 | 68 | 68 | 68
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 90 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 60 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 13.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-5-11_MS4-2012 |  | Customer |  |  |  | 2 |  | 2011.05.19
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-5-11_MS4-2033(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 40.1 | 60.2 | 79 | 100.8 | 120 | 149.5
Dis. Head | (m) | 98 | 92 | 85 | 75 | 58 | 38 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.014431 | 0.032525 | 0.056011 | 0.091189 | 0.12924 | 0.20059
Total Head | (m) | 98.5 | 92.5144 | 85.5325 | 75.556 | 58.5912 | 38.6292 | 0.70059
Water Power | (㎾) | 0 | 0.6047 | 0.8393 | 0.97293 | 0.96268 | 0.75559 | 0.017072
Shaft Power | (㎾) | 0.9139 | 1.2913 | 1.4874 | 1.6384 | 1.7901 | 1.8641 | 1.8485
Pump Eff. | (%) | 0 | 46.8289 | 56.4271 | 59.3847 | 53.779 | 40.5345 | 0.92356
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.15 | 3.72 | 4.04 | 4.32 | 4.6 | 4.74 | 4.71
Motor Input | (㎾) | 1.235 | 1.745 | 2.01 | 2.214 | 2.419 | 2.519 | 2.498
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 90 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 60 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-5-11_MS4-2033 |  | Customer |  |  |  | 2 |  | 2011.01.17
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-5-15_MS4-3012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30.5 | 61 | 86.2 | 120.2 | 150.6
Dis. Head | (m) | 137.5 | 133.8 | 122 | 103 | 60 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0083487 | 0.033395 | 0.066686 | 0.12967 | 0.20355
Total Head | (m) | 138.5 | 134.8083 | 123.0334 | 104.0667 | 61.1297 | 1.2035
Water Power | (㎾) | 0 | 0.6702 | 1.2233 | 1.4622 | 1.1977 | 0.029544
Shaft Power | (㎾) | 1.3774 | 1.6649 | 2.0576 | 2.3224 | 2.5631 | 2.5042
Pump Eff. | (%) | 0 | 40.2534 | 59.4544 | 62.9604 | 46.7281 | 1.1798
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 8.85 | 10.68 | 13.2 | 14.99 | 16.72 | 16.27
Motor Input | (㎾) | 1.94 | 2.345 | 2.898 | 3.271 | 3.61 | 3.527
Motor Eff. | (%) | 71 | 71 | 71 | 71 | 71 | 71
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 90 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 90 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 16.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 71 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-5-15_MS4-3012 |  | Customer |  |  |  | 2 |  | 2011.05.19
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-5-15_MS4-3033(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 30 | 60 | 86.6 | 120.5 | 155.2
Dis. Head | (m) | 136 | 131 | 120 | 100 | 60 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0080772 | 0.032309 | 0.067306 | 0.13031 | 0.21617
Total Head | (m) | 137 | 132.0081 | 121.0323 | 101.0673 | 61.1303 | 1.2162
Water Power | (㎾) | 0 | 0.64552 | 1.1837 | 1.4266 | 1.2007 | 0.030766
Shaft Power | (㎾) | 1.365 | 1.6845 | 2.112 | 2.412 | 2.6475 | 2.604
Pump Eff. | (%) | 0 | 38.3211 | 56.0462 | 59.1478 | 45.3519 | 1.1815
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.87 | 5.3 | 5.94 | 6.43 | 6.84 | 6.74
Motor Input | (㎾) | 1.82 | 2.246 | 2.816 | 3.216 | 3.53 | 3.472
Motor Eff. | (%) | 75 | 75 | 75 | 75 | 75 | 75
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 90 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 90 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 40 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 75 | Maker | 수모터 | Turbin | 0
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-5-15_MS4-3033 |  | Customer |  |  |  | 2 |  | 2010.11.10
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-5-26_MS4-5533
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA | [6 empty] | 단절 | 234m
Capacity | (㎥/min) | 0 | 0.025 | 0.05 | 0.075 | 0.09 | 0.11 | 0.13 | 0.15
Dis. Head | (m) | 235 | 232 | 221 | 195 | 174 | 135 | 83 | 20
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0056092 | 0.022437 | 0.050483 | 0.072695 | 0.10859 | 0.15167 | 0.20193
Total Head | (m) | 236.65 | 233.6556 | 222.6724 | 196.7005 | 175.7227 | 136.7586 | 84.8017 | 21.8519
Water Power | (kW) | 0 | 0.95215 | 1.8148 | 2.4047 | 2.5779 | 2.4521 | 1.7969 | 0.53428
Shaft Power | (kW) | 2.4178 | 2.772 | 3.4804 | 4.0887 | 4.389 | 4.7047 | 4.7432 | 4.5815
Pump Eff. | (%) | 0 | 34.3487 | 52.1429 | 58.8124 | 58.7344 | 52.1198 | 37.8847 | 11.6617
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 7.07 | 7.58 | 8.8 | 9.9 | 10.44 | 11.02 | 11.09 | 10.78
Motor Input | (kW) | 3.14 | 3.6 | 4.52 | 5.31 | 5.7 | 6.11 | 6.16 | 5.95
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.09 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 4.0 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 160 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 |  | 40 | 1.65
Efficiency |  | (%) | Volt.(v) | 380 | Current(A) | 11.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 77 | M/T Maker | sumoto | MAGNET | 20 | 18.5
Item No. |  |  | Serial No. |  | Inspector | JUNG.Y.J | Run (Hr) | B/R (℃) | Test Date
Model | PS-5-26_MS4-5533 |  | Customer |  |  |  | 2 | 0 | 2011.05.07
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification