## Datasheet(9-6)
Submersible Motor Pump Data Sheet
1 | Model | PS-9-6_MS4-2012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 37 | m | Discharge Piece | STS304
10 | Rated Capacity | 150 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 50 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 53 | % | Pump Shaft | STS304
14 | Min. Flow | 80 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 13.5 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 356 | mm | Pump | 3.4 | kg
37 | Motor | 375 | mm | Motor | 14 | kg
38 | Total | 731 | mm | Total | 17.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(9-6)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-9-6_MS4-2033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 37 | m | Discharge Piece | STS304
10 | Rated Capacity | 150 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 50 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 53 | % | Pump Shaft | STS304
14 | Min. Flow | 80 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 1.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 4.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 6 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 356 | mm | Pump | 3.4 | kg
37 | Motor | 340 | mm | Motor | 11.4 | kg
38 | Total | 696 | mm | Total | 14.8 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(9-8)
Submersible Motor Pump Data Sheet
1 | Model | PS-9-8_MS4-3012 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 52 | m | Discharge Piece | STS304
10 | Rated Capacity | 150 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 70 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 53 | % | Pump Shaft | STS304
14 | Min. Flow | 80 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | Low Carbon Steel
22 | Power Supply | 1 phase 220 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 16.9 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 418 | mm | Pump | 4 | kg
37 | Motor | 430 | mm | Motor | 16.4 | kg
38 | Total | 848 | mm | Total | 20.4 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(9-8)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-9-8_MS4-3033 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 52 | m | Discharge Piece | STS304
10 | Rated Capacity | 150 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 70 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 53 | % | Pump Shaft | STS304
14 | Min. Flow | 80 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 2.2 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 4.85 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 306 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 8 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 418 | mm | Pump | 4 | kg
37 | Motor | 375 | mm | Motor | 14.2 | kg
38 | Total | 793 | mm | Total | 18.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(9-14)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-9-14_MS4-5533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 90 | m | Discharge Piece | STS304
10 | Rated Capacity | 150 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 125 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 53 | % | Pump Shaft | STS304
14 | Min. Flow | 80 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 4 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 11.2 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 14 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 604 | mm | Pump | 5.7 | kg
37 | Motor | 555 | mm | Motor | 23.4 | kg
38 | Total | 1159 | mm | Total | 29.1 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Datasheet(9-21)3P
Submersible Motor Pump Data Sheet
1 | Model | PS-9-21_MS4-7533 | Agent No. |  | Sheet No.
2 | Customer |  | Item No. |  | Quantity
3 | Plant Name |  | Location |  | Issued Date
4 | Operating Condition
5 | Liquid Pumped | Water |  | PH | PH 5.8 ~ 8.6
6 | Liquid Temperature | 4 ~ 40 | ℃ | Max. Particle Dia. | 0.25 | mm
7 | Specific Gravity | 1 |  | Installation | Vertical & Horizontal
8 | Pump Design Data |  |  | Pump Materials
9 | Rated Total Head | 140 | m | Discharge Piece | STS304
10 | Rated Capacity | 150 | ℓ/min | Impeller | Noryl
11 | Shut off Head | 185 | m | Diffuser | Polycarbonate
12 | Speed | 3450 | rpm | Suction Piece | STS304
13 | Rated Efficiency | 53 | % | Pump Shaft | STS304
14 | Min. Flow | 80 | ℓ/min | Coupling | STS304
15 | Max. Flow | 230 | ℓ/min | Shell | STS304
16 | Discharge Dia. | 50 | mm | Strainer | STS304
17 | Out Dia. | 98mm(Cable Guard included) |  | Cable Guard | STS304
18 | Motor Design Data |  |  | Motor Materials
19 | Manufacturer | SUMOTO |  | Stator Shell | STS304
20 | Type | Submersible Motor |  | Shaft | STS303
21 | Rated Power | 5.5 | kw | Stud | Low Carbon Steel
22 | Power Supply | 3 phase 380 volt 60 Hz |  | Seal Cover | STS304&Sintered Bronze
23 | Pole | 2 | p | Seal | Carbon Ceramic Face
24 | Max. Load Current | 15.6 | A | Diaphragm | Nitrile
25 | Insulation Class | F | class | Diaphragm Cover | STS302
26 | Operating Cond. | Continuous |  | Slinger | Nitrile
27 | Starting Method | Direct On Line |  | Lead Potting | Epoxy
28 | Out Dia. | 95 | mm | Lead Jam Nut | STS304
29 | Max. downthrust | 663 kgf |  | Bearing/Sleeve | Carbon
30 | Constructions
31 | Impeller Type | Closed Type |  | Sealing Type | Oil Seal & Sand Collar (Motor)
32 | Flow Direction | Radial |  | Cooling | Water Cooling
33 | Stages | 21 | stages | Lubrication | Water Lubrication
34 | Discharge Conn. | Direct to Pipe |  | Rotation | CCW facing shaft end
35 | Length |  |  | Weight
36 | Pump | 859 | mm | Pump | 7.8 | kg
37 | Motor | 675 | mm | Motor | 29.4 | kg
38 | Total | 1534 | mm | Total | 37.2 | kg
| Remark |  |  | Prepared By | Checked By | Approved By

## Outline Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
SPECIFICATION
MODEL | MOTOR | STAGES |  |  | POWER RESOURCE
[5 empty] | HP |  | PHASE | VOLTS | HZ
PS-9-6 | MS4-2012 | 6 |  |  | 2 |  | 1 | 220 | 60
| MS4-2033 | [5 empty] | 3 | 380 | 60
PS-9-8 | MS4-3012 | 8 |  |  | 3 |  | 1 | 220 | 60
| MS4-3033 | [5 empty] | 3 | 380 | 60
PS-9-14 | MS4-5533 | 14 |  |  | 5 |  | 3 | 380 | 60
PS-9-21 | MS4-7533 | 21 |  |  | 7 |  | 3 | 380 | 60
DIEMENSION(mm)
MODEL | MOTOR | P.L |  |  | M.L |  |  | T.L
PS-9-6 | MS4-2012 | 356 |  |  | 375 |  |  | 731
| MS4-2033 |  |  |  | 340 |  |  | 696
PS-9-8 | MS4-3012 | 418 |  |  | 430 |  |  | 848
| MS4-3033 |  |  |  | 375 |  |  | 793
PS-9-14 | MS4-5033 | 604 |  |  | 555 |  |  | 1159
PS-9-21 | MS4-7533 | 859 |  |  | 675 |  |  | 1534
WEIGHT(kg)
MODEL | MOTOR | PUMP |  |  | MOTOR |  |  | TOTAL
PS-9-6 | MS4-2012 | 3.4 |  |  | 14 |  |  | 17.4
| MS4-2033 |  |  |  | 11.4 |  |  | 14.8
PS-9-8 | MS4-3012 | 4 |  |  | 16.4 |  |  | 20.4
| MS4-3033 |  |  |  | 14.2 |  |  | 18.2
PS-9-14 | MS4-5033 | 5.7 |  |  | 23.4 |  |  | 29.1
PS-9-21 | MS4-7533 | 7.8 |  |  | 29.4 |  |  | 37.2
※MOTOR MAKER : SUMOTO
※DISCHARGE CONNECTION : 2"
|  |  | TYPE |  |  | SUBMERSIBLE PUMP
MODEL
SERVICE
|  |  | SCALE:N/S |  |  |  | 3rd. ANGLE PROJECT
Outline Drawing
of PS-9 Series
P.L
M.L
T.L

## Sectional Drawing
Sheet No.
CUSTOMER
ITEM No.
DATE
NO | PART NAME |  |  | MATERIAL |  | Q'TY
1 | Discharge |  |  | STS304
2 | Valve Casing |  |  | STS304
4 | Valve Cone |  |  | STS304
6 | Valve Retaining Ring |  |  | STS304
9 | Adapter Ring |  |  | STS304
10 | Bearing Spider |  |  | STS304
12 | Diffuser |  |  | Polycarbonate
13 | Bowl |  |  | STS304
18 | Impeller |  |  | nPPO
24 | Stop Ring |  |  | STS304
34 | Strainer |  |  | STS304
36 | Suction Interconnector |  |  | STS304
40 | Pump Shaft/ Coupling |  |  | STS304
41 | Shaft Retaining Ring |  |  | STS304
42 | Shaft Sleeve |  |  | STS304
48 | Casing |  |  | STS304
52 | Cable Guard |  |  | STS304
86 | O-ring |  |  | NVR
87 | O-ring |  |  | NVR
88 | Screw |  |  | STS304
89 | Washer |  |  | STS304
90 | Bearing Spider |  |  | STS304
92 | Washer |  |  | STS304
|  | TYPE |  | SUBMERSIBEL PUMP
MODEL
SERVICE
|  | SCALE:N/S |  |  | 3rd. ANGLE PROJECT
Sectional Drawing
of PS-9 Series
88
36
34
89
48
52
88
40
10
2
18
13
12
24
90
9
6
1
92
42
41
87
86
4

## PS-9-6_MS4-2012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50.4 | 100.6 | 150.7 | 200 | 275.3
Dis. Head | (m) | 54.5 | 51.8 | 46.5 | 40 | 28 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0093377 | 0.037203 | 0.083484 | 0.14704 | 0.27861
Total Head | (m) | 55.5 | 52.8093 | 47.5372 | 41.0835 | 29.147 | 1.2786
Water Power | (㎾) | 0 | 0.43384 | 0.77951 | 1.0092 | 0.95019 | 0.057376
Shaft Power | (㎾) | 0.91664 | 1.1696 | 1.4545 | 1.7204 | 1.8006 | 1.6252
Pump Eff. | (%) | 0 | 37.093 | 53.5919 | 58.6595 | 52.7698 | 3.5304
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 8.16 | 9.42 | 11.05 | 12.78 | 13.27 | 12
Motor Input | (㎾) | 1.348 | 1.72 | 2.139 | 2.53 | 2.648 | 2.39
Motor Eff. | (%) | 68 | 68 | 68 | 68 | 68 | 68
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 150 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 37 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 13.5 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 68 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-9-6_MS4-2012 |  | Customer |  |  |  | 2 |  | 2011.05.20
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-9-6_MS4-2033(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 60 | 100 | 152.5 | 200.7 | 250.6 | 278.2
Dis. Head | (m) | 54.5 | 51 | 46 | 40 | 29 | 12 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013234 | 0.03676 | 0.085491 | 0.14807 | 0.23086 | 0.28451
Total Head | (m) | 55 | 51.5132 | 46.5368 | 40.5855 | 29.6481 | 12.7309 | 0.78451
Water Power | (㎾) | 0 | 0.5038 | 0.75855 | 1.0089 | 0.96991 | 0.52003 | 0.035575
Shaft Power | (㎾) | 0.8732 | 1.2188 | 1.4482 | 1.7279 | 1.8285 | 1.7235 | 1.6635
Pump Eff. | (%) | 0 | 41.3364 | 52.3795 | 58.3861 | 53.0429 | 30.1735 | 2.1385
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 3.09 | 3.61 | 3.98 | 4.49 | 4.67 | 4.48 | 4.37
Motor Input | (㎾) | 1.18 | 1.647 | 1.957 | 2.335 | 2.471 | 2.329 | 2.248
Motor Eff. | (%) | 74 | 74 | 74 | 74 | 74 | 74 | 74
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 150 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 1.5 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 37 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 0.5
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 4.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 74 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-9-6_MS4-2033 |  | Customer |  |  |  | 2 |  | 2011.01.17
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-9-8_MS4-3012(220V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50.6 | 100 | 132.3 | 200.4 | 279.3
Dis. Head | (m) | 73.5 | 69.8 | 63 | 58 | 38.5 | 1
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.009412 | 0.03676 | 0.064343 | 0.14763 | 0.28676
Total Head | (m) | 74.5 | 70.8094 | 64.0368 | 59.0643 | 39.6476 | 2.2868
Water Power | (㎾) | 0 | 0.58402 | 1.0438 | 1.2737 | 1.2951 | 0.10411
Shaft Power | (㎾) | 1.2311 | 1.5663 | 1.9362 | 2.1769 | 2.3835 | 2.0959
Pump Eff. | (%) | 0 | 37.2877 | 53.9105 | 58.5116 | 54.3367 | 4.9671
Speed | (rpm)
Voltage | (V) | 220 | 220 | 220 | 220 | 220 | 220
Current | (A) | 8.06 | 10.17 | 12.56 | 14.22 | 15.59 | 13.64
Motor Input | (㎾) | 1.734 | 2.206 | 2.727 | 3.066 | 3.357 | 2.952
Motor Eff. | (%) | 71 | 71 | 71 | 71 | 71 | 71
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 150 | (ℓ/min) | Phase (Φ) | 1 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 52 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 220 | Current(A) | 16.9 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 71 | Maker | SUMOTO | Turbin
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-9-8_MS4-3012 |  | Customer |  |  |  | 2 |  | 2011.05.20
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-9-8_MS4-3033(380V)
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA
Capacity | (ℓ/min) | 0 | 50 | 100 | 174.7 | 200.4 | 251 | 289
Dis. Head | (m) | 74 | 69 | 63 | 50 | 42 | 19 | 0
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.03676 | 0.11219 | 0.14763 | 0.23159 | 0.30703
Total Head | (m) | 75 | 70.0092 | 64.0368 | 51.1122 | 43.1476 | 20.2316 | 1.307
Water Power | (㎾) | 0 | 0.57057 | 1.0438 | 1.4555 | 1.4094 | 0.82774 | 0.06157
Shaft Power | (㎾) | 1.2263 | 1.5735 | 1.9507 | 2.4383 | 2.4675 | 2.331 | 2.1465
Pump Eff. | (%) | 0 | 36.2615 | 53.5076 | 59.6935 | 57.1196 | 35.5099 | 2.8684
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 4.78 | 5.18 | 5.68 | 6.44 | 6.49 | 6.26 | 5.92
Motor Input | (㎾) | 1.635 | 2.098 | 2.601 | 3.251 | 3.29 | 3.108 | 2.862
Motor Eff. | (%) | 75 | 75 | 75 | 75 | 75 | 75 | 75
■ SPECIFICATION FOR PUMP & MOTOR
PUMP SPECIFICATION |  |  | MOTOR SPECIFICATION |  |  |  | TEST CONDITION
Capacity | 150 | (ℓ/min) | Phase (Φ) | 3 | Output(㎾) | 2.2 | S/Pipe(mm) | D/Pipe(mm) | H/Diff.(m)
Total Head | 52 | (m) | Pole (P) | 2 | Freq.(Hz) | 60 |  | 50 | 1
Efficiency |  | (%) | Volt. (V) | 380 | Current(A) | 6.85 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff. (%) | 75 | Maker | 수모터 | Turbin | 0
Item No. |  |  | Serial No. |  | Inspector | K.J.O | Run (Hr) | B/R (℃) | Test Date
Model | PS-9-8_MS4-3033 |  | Customer |  |  |  | 2 |  | 2010.11.10
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 6.6 | 7.1 | 7.77 | 8.6 | 9.37 | 9.9 | 10.67 | 11.1
380V일때의 전류치 |  | 3.8211 | 4.1105 | 4.4984 | 4.9789 | 5.4247 | 5.7316 | 6.1774 | 6.4263
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-9-14_MS4-5533
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA | [6 empty] | 단절 | 129m
Capacity | (㎥/min) | 0 | 0.06 | 0.1 | 0.15 | 0.18 | 0.2 | 0.23 | 0.26
Dis. Head | (m) | 128.5 | 120.5 | 110.5 | 97.5 | 85 | 72.5 | 51 | 21.5
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.013234 | 0.03676 | 0.082711 | 0.1191 | 0.14704 | 0.19446 | 0.2485
Total Head | (m) | 130.15 | 122.1632 | 112.1868 | 99.2327 | 86.7691 | 74.297 | 52.8445 | 23.3985
Water Power | (kW) | 0 | 1.1948 | 1.8286 | 2.4262 | 2.5458 | 2.4221 | 1.9811 | 0.99163
Shaft Power | (kW) | 2.156 | 2.8336 | 3.4265 | 4.1503 | 4.3736 | 4.4044 | 4.3043 | 3.9347
Pump Eff. | (%) | 0 | 42.1639 | 53.3677 | 58.4594 | 58.2085 | 54.9924 | 46.027 | 25.2021
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 6.63 | 7.68 | 8.7 | 9.97 | 10.37 | 10.44 | 10.28 | 9.58
Motor Input | (kW) | 2.8 | 3.68 | 4.45 | 5.39 | 5.68 | 5.72 | 5.59 | 5.11
Motor Eff. | (%) | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.15 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 4.0 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 90 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 |  | 50 | 1.65
Efficiency |  | (%) | Volt.(v) | 380 | Current(A) | 11.2 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 77 | M/T Maker | sumoto | MAGNET | 20 | 18.5
Item No. |  |  | Serial No. |  | Inspector | JUNG.Y.J | Run (Hr) | B/R (℃) | Test Date
Model | PS-9-14_MS4-5533 |  | Customer |  |  |  | 2 | 0 | 2011.05.09
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification

## PS-9-21_MS4-7533
PUMP TEST REPORT
■ PERFORMANCE CURVE
■ PERFORMANCE DATA | [6 empty] | 단절 | 194m
Capacity | (㎥/min) | 0 | 0.05 | 0.1 | 0.15 | 0.175 | 0.2 | 0.24 | 0.26
Dis. Head | (m) | 194 | 185 | 168 | 147.5 | 132.5 | 110 | 70 | 40
Suc. Head | (m) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Speed Head | (m) | 0 | 0.0091901 | 0.03676 | 0.082711 | 0.11258 | 0.14704 | 0.21174 | 0.2485
Total Head | (m) | 195.65 | 186.6592 | 169.6868 | 149.2327 | 134.2626 | 111.797 | 71.8617 | 41.8985
Water Power | (kW) | 0 | 1.5213 | 2.7659 | 3.6487 | 3.8298 | 3.6446 | 2.8112 | 1.7757
Shaft Power | (kW) | 3.3852 | 4.2822 | 5.421 | 6.5208 | 6.7704 | 6.8094 | 6.591 | 6.1464
Pump Eff. | (%) | 0 | 35.5255 | 51.0218 | 55.9554 | 56.5674 | 53.5228 | 42.6526 | 28.8894
Speed | (rpm)
Voltage | (V) | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380
Current | (A) | 9.91 | 11.3 | 13.27 | 15.24 | 15.7 | 15.77 | 15.4 | 14.5
Motor Input | (kW) | 4.34 | 5.49 | 6.95 | 8.36 | 8.68 | 8.73 | 8.45 | 7.88
Motor Eff. | (%) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
■ SPECIFICATION FOR PUMP & MOTOR
Pump Specification |  |  | Motor Specification |  |  |  | Test Condition
Capacity | 0.15 | (㎥/min) | Phase(Φ) | 3 | Output(kW) | 5.5 | S/Pipe Φ | D/Pipe Φ | H/Diff. m
Total Head | 140 | (m) | Pole(P) | 2 | Freq.(Hz) | 60 |  | 50 | 1.65
Efficiency |  | (%) | Volt.(v) | 380 | Current(A) | 15.6 | Flow Meter | R.T (℃) | W.T (℃)
I/P Out-Dia |  | (mm) | Eff.(%) | 78 | M/T Maker | sumoto | MAGNET | 20 | 18.5
Item No. |  |  | Serial No. |  | Inspector | JUNG.Y.J | Run (Hr) | B/R (℃) | Test Date
Model | PS-9-21_MS4-7533 |  | Customer |  |  |  | 2 | 0 | 2011.05.06
Checked By |  |  |  |  | Approved By
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suc. Head | m | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum | mmhg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220V일때의 전류치 |  | 11.98 | 13.62 | 14.59 | 16.52 | 18.1 | 19.43 | 21.67
440V일때의 전류치 |  | 20.6927 | 23.5255 | 25.2009 | 28.5345 | 31.2636 | 33.5609 | 37.43 | 0
|  | 0 | 75 | 167 | 210 | 278 | 363 | 405
|  | 0 | 1.019 | 2.269 | 2.8533 | 3.7772 | 4.9321 | 5.5027
□ Total Head ㅇ Pump Eff. △ Shaft Power X Specification